## Slide 1
NOGRR 245
TAC
Stephen Solis – Principal, System Operations Improvement
January 24th, 2024

## Slide 2: Overview
Multiple events have occurred where Inverter Based Resources (IBRs) failed to ride-through
  Magnitudes have increased with more IBRs on ERCOT System
As proposed by ERCOT, Nodal Operating Guide Revision Request (NOGRR 245) would enhance clarity and specificity of IBR ride through requirements and align with most relevant parts of IEEE 2800-2022 and NERC Reliability Guidelines
ERCOT received over 50 public comments and multiple separate feedback meetings on NOGRR 245
FERC issued Order 901 directing NERC to address same risks that NOGRR245 addresses
ERCOT presented RFI results from OEMs and REs on ability to comply with ERCOT proposal and ROS-recommended versions of NOGRR at December TAC meeting
Presentation summarizes proposed changes based on the information obtained through this RFI

## Slide 3: ERCOT Proposed Changes to NOGRR 245 (1/8/24)
Allows for additional exceptions for documented technical limitations
  Must meet existing requirements, and substantially meet new requirements, with each plant's documented technical limitation level becoming the requirement for that plant
  Must maximize capability through use of parameterization, software upgrades and minor hardware upgrade kits. ERCOT proposed a bright line criteria to not require hardware upgrades that exceed 20% of the replacement cost on a per turbine/inverter basis.
  Cannot create any instability, uncontrolled separation, or cascading outages for the ERCOT system
  Technical limitations must be accurately represented in all provided models
  Must meet latest requirements upon reinvestment (e.g., repower/retrofit requiring GIM process)
Remove specificity and clarity requirements for legacy IBRs for RoCoF and Phase Angle Jump
  Return expectations around RoCoF and Phase Angle Jump requirements to status quo
    If voltage and frequency are within “no trip” zones, IBR must ride through
    Aligns with previous technical discussions that during transient, frequency and phase angle measurements are unreliable and IBR unit should not trip for these parameters during fault conditions.
Modified multiple excursion requirement for legacy IBRs to maximize capability if they use a counter and ensure they can ride through normal TSP reclose schemes vs current alignment with IEEE 2800
  Two major TSPs have indicated between 0 and 2 normal reclose attempts. ERCOT would consider a bright line criteria but would need TSPs to help identify such a criteria.
    1st attempt is within 1 second
    2nd attempt is between 10 and 20 seconds

## Slide 4: ERCOT Proposed Changes to NOGRR 245
Restored operational restrictions expectations for performance failures that pose significant reliability risk and cannot be implemented in reasonable time. Additional guardrails were proposed to limit the application of the restrictions to:
  When the actual or potential severity of the event on the ERCOT System is greater than the most severe single contingency.
  When the cause of the performance failure cannot be mitigated within 90 calendar days.
  When the location of the performance failure did affect or has the potential to materially affect known stability limitation on the ERCOT System
  When the IBR or WGR experience more than one failure in the prior 36 calendar months; or
  If the failure presents an imminent safety or equipment risk on the ERCOT system.
Other clarifications/exceptions
  Handling of active current reductions during fault
  SGIA modifications for load-only additions would not trigger requirement to meet IEEE 2800 requirements if IBR does not need physical modifications to meet other requirements
  Additional limited exceptions may be allowed for IBRs with SGIA after 6/1/23 and COD before 1/1/26 with documented limitations to fully meeting IEEE 2800-2022 standard.
  Additional extensions (up to 24 months) may be allowed for IBRs with SGIA after 6/1/23 after their COD to install upgrades to meet IEEE 2800-2022 standard requirements no later than 12/31/28.
  Allows for new IBRs to have slower response times than required if needed for reliability purposes but clarifies that SSR Mitigation shall not depend on those slower recovery rates (i.e. if both the required response times and SSR Mitigation are needed, the IBR must provide SSR mitigation that does not depend on slowing down the response).

## Slide 5: Reliability Impact of ERCOT proposed exceptions
Can move forward w/ OEM-identified parameterization and upgrade kits available from OEMs but that owners are waiting to authorize and procure
"Technical Infeasibility" exemptions would not require consideration of very expensive upgrades such as repowers or converter replacements"
Allows IBRs w/ SGIA beyond 6/1/23 with challenges to immediately meeting IEEE 2800 requirements to have a feasible path forward
Reliability risk continues due to IBRs w/ exemptions
Modeled limitations may impact stability limits
  Generic Transmission Constraints and its limits (GTLs) may be updated or added as needed.
  Impact of exceeding some GTLs may qualify them as an IROL
  Additional transmission projects may need to be implemented
Some newly modeled limitations and repeated performance failures may require new credible contingencies (e.g., combined transmission and generator contingency) to be considered in both operations and planning
  May result in additional transmission congestion
  May create new voltage, cascading or instability conditions
Key Takeaway: Proposed exemptions should help faster adoption of available improvements and IEEE 2800 but at expense of continued reliability risk and its associated impacts

## Slide 6: Additional assumptions
IBR performance requirements are one part of overall solution to address risk
  IBR performance requirements (NOGRR 245) w/ appropriate enforcement
  System strength upgrades (e.g., 6 new synchronous condensers)
  Grid Forming capability adoption
  Modeling and testing improvements (DWG/IBRWG collaboration)
  Disturbance monitoring equipment installs (NOGRR 255)
  Potential planning criteria adjustments
To offset risk, exemptions must be accompanied by:
  Clear expectations around potential operating restrictions for failures
  Models and contingencies accurately reflecting limitations
  Proper active and reactive power controls coordination
The actions required to offset the risk could lead to additional operation and planning impact such as congestion and system improvements.
Key Takeaway: Proposal assumes willingness to take on more reliability risk, that other risk offset activities will be adopted, and that other system cost impacts are acceptable to impacted entities.

## Slide 7: Evolution of NOGRR 245
Reliability Risk
Uncontrolled Loss of ERCOT system
IBR Owners impact
Insufficient Timelines
Mitigation Cost
Operational &Compliance Risk
Event Analysis
Reliability Risk
Controlled EEA Load Shed
Uncontrolled Loss of ERCOT system
IBR Owners impact
Insufficient Timelines & Technical Infeasibility
Mitigation Cost
Operational &Compliance Risk
Potential Retirements
Reliability Risk
Controlled EEA Load shed
Uncontrolled Loss of ERCOT system
IBR Owners impact
Insufficient Timelines & Technical Infeasibility
Mitigation Cost
Operational &Compliance Risk
Potential Retirements
Reliability Risk
Uncontrolled loss of ERCOT system
IBR Owners impact
Potential non-compliance
Event Analysis workload
Current Status
1/11/23 NOGRR 245 version
Reliability Risk
Controlled EEA Load Shed
Uncontrolled Loss of ERCOT system
IBR Owners impact
Insufficient Timelines & Technical Infeasibility
Mitigation Cost
Operational &Compliance Risk
Potential Retirements
4/5/23 NOGRR 245 version
8/14/23 NOGRR 245 version
Reliability Risk
Uncontrolled loss of ERCOT system
IBR Owners impact
Mitigation Cost
Event Analysis workload
Compliance Risk
ROS approved version
1/8/24 NOGRR 245 version
Residual Risk from Exemptions
Key Takeaway: Multiple iterations from ERCOT have taken input from owners and OEMs to balance the reliability risk and impact to IBR owners.

## Slide 8: Residual Impacts of Exemptions
Reliability Risk
Uncontrolled Loss of ERCOT system
IBR Owners impact
Insufficient Timelines
Mitigation Cost
Operational &Compliance Risk
Event Analysis
1/8/24 NOGRR 245 version
Residual Risk from Exemptions
Key Takeaway: Balancing the impact on IBR Owners and Reliability Risk impacts other Market Participants and customers.
Residual Risk from Exemptions
Impact on MPs & Customers
More ERCOT work for ops, planning, and event analysis
Potential for new stability limits/IROLs and congestion
Additional transmission upgrades may be needed
More compliance risk for ERCOT and other MPs
Loss of Firm Load
More ride-through failure events
1/8/24 NOGRR 245 version
FERC Order 901 requires that NERC ensures that the impacts of any limited exemptions are addressed by planners and operators.
To manage the risk, ERCOT must ensure the limitations reflected in planning and operations assessments to ensure the system remains N-1 secure.
  May result in new stability limits or congestion
  May result in additional transmission upgrades needed

## Slide 9: Proposed timeline for NOGRR 245 (i.e. Next steps)

## Slide 10: NOGRR 245 – ERCOT Recommendation
ERCOT strongly recommends the TAC members adopt the comments submitted by ERCOT on 1/8/24 which:
  Is technically feasible
  Incorporates 12 months of stakeholder and OEM feedback
  Balances reliability risk with impact on generator owners
  Aligns with FERC Order 901
  Aligns with NERC recommendations from the Odessa Event and NERC Reliability Guidelines
  Aligns new IBRs with IEEE-2800 IBR ride-through requirements with exception and extensions to account for this transition
ERCOT continues to recommend entities maximize ride-through capabilities w/o delay to minimize reliability risk to ERCOT System
Key Takeaway: ERCOT recommends approval of NOGRR 245 with its January 8, 2024 comments. The ROS-recommended proposal is not acceptable as it does not address the current, significant reliability risk.

## Slide 11
Questions?