## Slide 1
TNMP Pecos County Transmission Improvement Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
January 24, 2024

## Slide 2: Overview
TNMP submitted the TNMP Pecos County Transmission Improvement Project for Regional Planning Group (RPG) review in August 2023
  This is a Tier 1 project that was estimated to cost $108.0 million
  Addresses the reliability need in the Reeves and Ward Counties in the Far West weather zone under maintenance outage conditions

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review indicated reliability planning criteria violations
System improvement is needed to meet reliability planning criteria under maintenance outage conditions
Voltage Violations | Thermal Overloads | Unsolved Power Flow
26 | 52.2 miles of 138-kV line | 5

## Slide 5: Comparison of Project Options
ERCOT analyzed nine options and short-listed three options
Among the short-listed three options, Option 1 improves long-term load serving capability, operational flexibility, provides an additional load interconnection point and fastest estimated completion date
Option 1 is the preferred option
 | Option |  | 
 | 1 | 2 | 5
Address the project needs | Yes | Yes | Yes
Meets ERCOT and NERC Reliability Criteria | Yes | Yes | Yes
Improves Long-term Load Serving Capability | Yes (Better) | Yes (Better) | Yes
Improves Operational Flexibility | Yes (Better) | Yes | Yes
Provides Additional 138-kV Load Interconnection Point | Yes | No | No
Require CCN (miles) | ~ 31.1 | ~ 31.3 | ~ 22.0
Estimated Completion Date | Aug-26 | Apr-27 | May-27
Cost Estimate* ($M) | ~ 114.8 | ~ 114.3 | ~ 113.1
* Cost estimates and CCN mileage were provided by TSPs

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did not cause any new congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 1 to address the reliability need in the Reeves and Ward Counties in the Far West weather zone under maintenance outage conditions
TSP expects to implement the upgrades by August 2026
Estimated Capital Cost: $114.8 Million
ERCOT will recommend that the ERCOT Board designate Option 1 as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 9: ERCOT Recommendation: Option 1
Construct a new Coyanosa – Leon Creek 138-kV double‐circuit lines with rating of at least 717 MVA, will require approximately 31.1-mile of new Rights of Way (ROW)
Construct a new Woodhouse 138-kV substation by cutting into the existing Tarbush to Leon Creek 138-kV transmission line
Construct a new tie Woodhouse – Ft. Stockton SW 138-kV transmission line with a normal and emergency ratings of at least 717 MVA , approximately 0.1-mile
Rebuild the existing second circuit Rio Pecos – Girvin 138-kV transmission line with a normal and emergency ratings of at least 717 MVA, approximately 0.6-mile
Rebuild the existing Rio Pecos – Crane 138-kV transmission line with a normal and emergency ratings of at least 717 MVA, approximately 23.7-mile

## Slide 10: Option 1