## Slide 1
HDL/LDL Manual Override Report
WMS
Cory Carswell
Market Operations
February 7, 2024

## Slide 2: Introduction
Per protocol language section 6.5.7.1.13 (10):
  No sooner than sixty days after the applicable Operating Day, ERCOT shall provide to the appropriate TAC subcommittee instances of manual overrides of HDL or LDL, including the name of the Generation Resource, the reason for the override, and, as applicable, the cost as calculated in Section 6.6.3.6, Real-Time High Dispatch Limit Override Energy Payment.

## Slide 3: Manual Override Driver – DELMSAN5
Over five non-consecutive days, 37 resources had HDL or LDL manual overrides because the DELMSAN5: PAWNEE_SPRUCE constraint had exceeded its load shed rating, showing a potential risk of cascading outage if the constraint was not managed in a reasonable amount of time.
Days Affected:
August 10, 2023
August 11, 2023
August 17, 2023
September 6, 2023
September 7, 2023
Wind: 34
Coal: 1
Solar: 2
Resource Breakdown:
Intervals:
A total of 164 unique SCED Intervals were impacted:
August 10: 61 intervals
August 11: 28 intervals
August 17: 28 intervals
September 6: 29 intervals
September 7: 18 intervals
Cost:
The costs, as calculated in Section 6.6.3.6, is approximately $0.27M incurred by 1 Resource on three of the five Operating Days listed.

## Slide 4: Manual Override – Resource List
37 resources had manual HDL or LDL overrides at various times over the 5 days of 08/10/2023, 08/11/2023, 08/17/2023, 09/06/2023, and 09/07/2023 due to the constraint DELMSAN5: PAWNEE_SPRUCE, which had exceeded its load shed rating and posed a potential risk of a cascading outage if not managed within a reasonable amount of time.
ALGODON_UNIT1
ALGODON_UNIT2
FOXTROT_UNIT1
FOXTROT_UNIT2
FOXTROT_UNIT3
KARAKAW1_UNIT2
KARAKAW2_UNIT3
SANMIGL_G1
BRIGHTSD_UNIT1
RELOJ_UNIT1
RELOJ_UNIT2
RELOJ_UNIT3
CORAZON_UNIT1
TORR_UNIT1_25
TORR_UNIT2_23
TORR_UNIT2_25
BAFFIN_UNIT1
BAFFIN_UNIT2
PENA_UNIT1
PENA_UNIT2_J01
PENA_UNIT2_J02
TGW_T1
TGW_T2
BORDAS2_JAVEL2_A
BORDAS2_JAVEL2_B
BORDAS2_JAVEL2_C
BORDAS_JAVEL18
BORDAS_JAVEL20
CABEZON_WIND1
CABEZON_WIND2
LV3_UNIT_1
LV4_UNIT_1
MESTENO_UNIT_1
MIRASOLE_MIR11
MIRASOLE_MIR12
MIRASOLE_MIR13
MIRASOLE_MIR21

## Slide 5: Manual Override Driver – DELMSAN5 08/10/2023
(2023-08-10 15:50 - 2023-08-10 20:05); 52 Intervals:
  ALGODON_UNIT1
(2023-08-10 15:55 - 2023-08-10 20:05); 51 Intervals:
  ALGODON_UNIT2
(2023-08-10 15:55 - 2023-08-10 20:10); 51 Intervals:
  FOXTROT_UNIT1
  FOXTROT_UNIT2
  FOXTROT_UNIT3
(2023-08-10 16:00 - 2023-08-10 20:10); 50 Intervals:
  KARAKAW1_UNIT2
  KARAKAW2_UNIT3
(2023-08-10 16:05 - 2023-08-10 20:00); 48 Intervals:
  SANMIGL_G1

## Slide 6: Manual Override Driver – DELMSAN5 08/11/2023
(2023-08-11 18:05 - 2023-08-11 19:50); 21 Intervals:
  FOXTROT_UNIT1
  FOXTROT_UNIT2
  FOXTROT_UNIT3
(2023-08-11 18:10 - 2023-08-11 19:50); 20 Intervals:
  ALGODON_UNIT1
  ALGODON_UNIT2
  KARAKAW1_UNIT2
  KARAKAW2_UNIT3
  SANMIGL_G1

## Slide 7: Manual Override Driver – DELMSAN5 08/17/2023
(2023-08-17 19:00 - 2023-08-17 20:32); 19 Intervals:
  ALGODON_UNIT1
  ALGODON_UNIT2
  BRIGHTSD_UNIT1
  FOXTROT_UNIT1
  FOXTROT_UNIT2
  FOXTROT_UNIT3
  KARAKAW1_UNIT2
  KARAKAW2_UNIT3
  RELOJ_UNIT1
  RELOJ_UNIT2
  RELOJ_UNIT3
(2023-08-17 19:05 - 2023-08-17 20:32); 18 Intervals:
  CORAZON_UNIT1
(2023-08-17 19:05 - 2023-08-17 20:35); 18 Intervals:
  TORR_UNIT1_25
  TORR_UNIT2_23
  TORR_UNIT2_25
(2023-08-17 19:15 - 2023-08-17 20:35); 16 Intervals:
  SANMIGL_G1

## Slide 8: Manual Override Driver – DELMSAN5 09/06/2023
(2023-09-06 18:40 - 2023-09-06 20:30); 23 Intervals:
  FOXTROT_UNIT1
  FOXTROT_UNIT2
  FOXTROT_UNIT3
(2023-09-06 18:45 - 2023-09-06 19:45); 13 Intervals:
  SANMIGL_G1
(2023-09-06 18:45 - 2023-09-06 20:25); 21 Intervals:
  ALGODON_UNIT1
  ALGODON_UNIT2
  CORAZON_UNIT1
  KARAKAW1_UNIT2
  KARAKAW2_UNIT3
(2023-09-06 18:50 - 2023-09-06 19:25); 8 Intervals:
  TORR_UNIT1_25
  TORR_UNIT2_23
  TORR_UNIT2_25
(2023-09-06 18:50 - 2023-09-06 20:20); 19 Intervals:
  RELOJ_UNIT1
  RELOJ_UNIT2
  RELOJ_UNIT3

## Slide 9: Manual Override Driver – DELMSAN5 09/06/2023
(2023-09-06 18:55 - 2023-09-06 19:21); 6 Intervals:
  BAFFIN_UNIT1
  BAFFIN_UNIT2
  PENA_UNIT1
  PENA_UNIT2_J01
  PENA_UNIT2_J02
(2023-09-06 18:55 - 2023-09-06 19:30); 8 Intervals:
  TGW_T1
  TGW_T2
(2023-09-06 18:55 - 2023-09-06 20:10); 16 Intervals:
  BRIGHTSD_UNIT1
(2023-09-06 19:05 - 2023-09-06 20:05); 13 Intervals:
  BORDAS2_JAVEL2_A
  BORDAS2_JAVEL2_B
  BORDAS2_JAVEL2_C
  BORDAS_JAVEL18
  BORDAS_JAVEL20

## Slide 10: Manual Override Driver – DELMSAN5 09/06/2023
(2023-09-06 19:10 - 2023-09-06 19:25); 3 Intervals:
  MIRASOLE_MIR11
  MIRASOLE_MIR12
  MIRASOLE_MIR13
  MIRASOLE_MIR21
(2023-09-06 19:10 - 2023-09-06 19:45); 8 Intervals:
  CABEZON_WIND1
  CABEZON_WIND2
(2023-09-06 19:10 - 2023-09-06 19:56); 10 Intervals:
  LV3_UNIT_1
  LV4_UNIT_1
(2023-09-06 19:10 - 2023-09-06 20:00); 11 Intervals:
  MESTENO_UNIT_1

## Slide 11: Manual Override Driver – DELMSAN5 09/07/2023
(2023-09-07 19:05 - 2023-09-07 20:15); 14 Intervals:
  FOXTROT_UNIT1
  FOXTROT_UNIT2
  FOXTROT_UNIT3
  KARAKAW1_UNIT2
  KARAKAW2_UNIT3
(2023-09-07 19:10 - 2023-09-07 20:15); 14 Intervals:
  ALGODON_UNIT1
  ALGODON_UNIT2
  BRIGHTSD_UNIT1
(2023-09-07 19:45 - 2023-09-07 20:05); 5 Intervals:
  RELOJ_UNIT1
  RELOJ_UNIT2
  RELOJ_UNIT3
  TORR_UNIT1_25
  TORR_UNIT2_23
  TORR_UNIT2_25
(2023-09-07 19:45 - 2023-09-07 20:15); 7 Intervals:
  CORAZON_UNIT1