## Slide 1
ERCOT Frequency Control Report
January 2024
ERCOT
Operations Planning
PDCWG | February 14, 2024

## Slide 2: Summary of January 2024
CPS1: 177.36%
Current CPS1 12-Month Rolling Average: 175.27%
0 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2022
2022 BAAL-003 FRM Performance: -1060.40
2024 RMS1 Statistics
  Mean: 14.24 mHz
  Min: 11.97 mHz
  Max 16.81 mHz
Energy Statistics
  Total Energy: 38,278,215 MWh
  Wind Energy: 8,544,849 MWh
  Percent Energy from Wind: 22.32%
  Solar Energy: 2,231,358 MWh
  Percent Energy from Solar: 5.83%
Minimum System Inertia
  Mean: 245,293 MW*s
  Max: 360,855 MW*s on January 15th
  Min: 160,920 MW*s on January 7th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jan-24 CPS1 (%): 177.36
Notes: Jan. CPS1 Score is 177.36%, there are no outliers below 100%.

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in January.

## Slide 6: 15-Minute Average CPS1%
Jan-24 CPS1 (%): 177.36
Notes: CPS1 score is above 150% for 15-minute intervals.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 175.27%
Notes: 12 month rolling average CPS1 score is 175.27 which is in line with expectations, and the CPS1 score for January is consistent with last month.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is slightly smaller overall compared with 2022.
  2024 Stats:
  Mean: 14.24 mHz
  Min: 11.97 mHz
  Max 16.81 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
14.24 mHz on avg for January 2024

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between January 2023 and January 2024. Compared to last year, there are more instances of frequency hovering around the dead bands.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile between January 2022 and January 2024. Similar to the previous slide, compared to 2022, there are more instances of frequency hovering around the dead bands.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2022 BAL-003 Selected Events – Update
Notes: BAL-003
These events will be selected and posted after April 1st, slide will be updated for upcoming PDCWG meetings.

## Slide 19: Op. Year 2022 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO = -471.0, FRM median = -913.56, FRM average = -992.
OP2022: FRO = -463.0, FRM median = -1060.40, FRM average = -1153.4

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 38,278,215 MWh

## Slide 22: Total Energy from Wind Generation
Notes:   8,544,849 MWH ~

## Slide 23: % Energy from Wind Generation
Notes: 22.32% of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 2,231,358 MWh ~ significant increase in solar from previous years.

## Slide 25: % Energy from Solar Generation
Notes: 5.83% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia = 160,920 MW*s on 1/07/2024
Previous Overall Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 245,293 MW*s
Max: 360,855 MW*s on January 15th
Min: 160,920 MW*s on January 7th

## Slide 28: ERCOT Inertia 2013-2024
Date and Time | 2013 3/10 3:00 AM | 2014 3/30 3:00 AM | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 00:00 AM | 2022 03/21 01:00 AM | 2023 04/18 02:00 AM | 2024 01/07 03:00 PM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 109 | 115 | 124 | 161
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 32,599 | 33,365 | 35,799 | 43,596
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53 | 50 | 57 | 65 | 66 | 61 | 66
Notes: Summary of ERCOT intertia for the previous 10 years. Lowest inertia this year was on January 7th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 29: Questions?
Thank you!