| PGRR Number | 114 | PGRR Title | Related to NPRR1212, Clarification of Distribution Service Provider’s Obligation to Provide an ESI ID |
| --- | --- | --- | --- |
| Date |  | February 22, 2024 |  |

| Submitter’s Information |  |
| --- | --- |
| Name | Martha Henson; Chris Rowley |
| E-mail Address | martha.henson@oncor.com; chris.rowley@oncor.com |
| Company | Oncor Electric Delivery Company LLC |
| Phone Number | 214-486-3432 |
| Cell Number | 214-536-9004 |
| Market Segment | Investor-Owned Utility |

Comments

Oncor supports Planning Guide Revision Request (PGRR) 114 and, in these comments, proposes to describe the Resource Entity’s responsibility to request an Electric Service Identifier (ESI ID) from its Distribution Service Provider (DSP) and provide it to ERCOT.

These comments work in concert with Oncor’s comments to Nodal Protocol Revision Request (NPRR) 1212, Clarification of Distribution Service Provider’s Obligation to Provide an ESI ID, which propose to describe the roles of the Resource Entity and the DSP serving the Resource Entity’s auxiliary Load in more detail in Protocol Section 10.3.2, ERCOT-Polled Settlement Meters.

Revised Cover Page Language

None

Revised Proposed Guide Language

5.5	Generator Commissioning and Continuing Operations

(1)	For each interconnecting Generation Resource or Energy Storage Resource (ESR), each Interconnecting Entity (IE) shall meet the conditions established by ERCOT before proceeding to Initial Energization, Initial Synchronization, and commercial operations.  These conditions may require proof of meeting applicable ERCOT requirements, which may include, but are not limited to, reactive capability, voltage ride-through standards, dynamic model template submission, Automatic Voltage Regulator (AVR), Primary Frequency Response, Power System Stabilizer (PSS), Subsynchronous Resonance (SSR) models, and telemetry.

- Before ERCOT approves Initial Energization for a project that will consume Load other than Wholesale Storage Load (WSL) and that is not behind a Non-Opt-In Entity (NOIE) tie meter:

(a)	The Resource Entity must request an Electric Service Identifier(s) (ESI ID(s)) from the Distribution Service Provider(s) (DSP(s)) that will be serving the Load at the Resource site and provide the ESI ID(s) to ERCOT, as described in paragraph (2) of Protocol Section 10.3.2, ERCOT-Polled Settlement Meters; and

(b)	These ESI ID(s) must be established in the ERCOT Settlement system in a state that allows for the Load to be properly settled to the appropriate Qualified Scheduling Entity (QSE).

(3)	Within 300 days of receiving ERCOT’s approval for Initial Synchronization above 20 MVA of a new or repowered Generation Resource or ESR, a Resource Entity shall ensure the Resource meets the conditions established by ERCOT for commercial operations and shall submit a request to ERCOT to commission the Resource.

(a)	In the event a Generation Resource or ESR will be unable to complete all necessary construction and required testing to commence commercial operations and connect reliably to the ERCOT System within the 300 days, the Generation Resource or ESR may request a good cause exception with sufficient detail, and shall notify ERCOT prior to the planned commercial operation date and provide ERCOT with an updated commercial operation date that the Generation Resource or ESR can reasonably expect to commence operations in a reliable manner.

(4)	No later than 30 days following the Resource Commissioning Date, the Resource Entity shall submit updates to the resource dynamic planning and operations models based on “as-built” or “as-tested” data and provide a plant verification report as required by paragraph (5)(b) of Section 6.2, Dynamics Model Development.  Pursuant to paragraph (5)(c) of Section 6.2, the IE shall include model updates with model quality tests.

(5)	During continuing operations:

(a)	Pursuant to paragraph (5)(c) of Section 6.2, the Resource Entity shall include model updates with model quality tests.

(b)	The Resource Entity shall provide ERCOT with a plant verification report as required by paragraph (5)(b) of Section 6.2 at the following times:

(i)	No later than 30 days after implementing a settings change as required by paragraph (7) of Section 6.2;

(ii)	No earlier than 12 months and no later than 24 months following the later of the Resource Commissioning Date or March 1, 2021; and

(iii)	A minimum of every ten years.