## Slide 1
Odessa Events Update &
Follow up Efforts
Patrick Gravois
Operations Engineer – Operations Analysis
IBRWG Meeting
March 8, 2024

## Slide 2: TMEIC Facilities Update
Corrective actions identified and implemented for systemic issues
  PLL Loss of Synch – Disable (Odessa 2021)
  Volt Phase Jump – Disable or increase threshold to 35⁰
  AC Overvoltage – Increase threshold to 1.4pu; decrease k- factor
  AC Overcurrent – Implement overcurrent mitigation firmware update developed by TMEIC
All the above have been implemented in the field for Odessa affected facilities with the following exceptions:
  Plant B – Have not implemented K-factor reduction due to decision to model first (did not trip on overvoltage)
  Plant C/D – Have not implemented overcurrent mitigation; waited on model approval before scheduling additional field work (did not trip on AC overcurrent protection)
Only 2 out of affected 8 facilities have provided updated models to ERCOT.
  Per Planning Guides, RE has 30 days to resubmit models once changes are made in the field
  ERM included which facilities had not resubmitted models in Odessa report to PUCT
  ERCOT will continue to follow up with REs to get these models updated, submitted, and approved

## Slide 3: TMEIC Facilities Update

## Slide 4: Follow up with Other Facilities with TMEIC inverters
ERCOT sent out a Market Notice on Sept. 8, 2023, instructing REs owning facilities with TMEIC inverters to perform the following actions:
  Consult with TMEIC to determine if AC overcurrent mitigation firmware update needs to be implemented at their facility or facilities.
  Consult with TMEIC about recommendations regarding overvoltage protection settings, PDR setting (Volt Phase Jump), ramp rate settings, etc.
  If updates and/or settings changes are required, the RE should schedule a date for TMEIC to implement required changes at the facility.
  By Oct. 20, 2023, RE shall notify ERCOT with either:
    A statement that the inverters already have the overcurrent mitigation update and recommended protection settings; or
    A plan and timeline for implementing the necessary changes
ERCOT tracked responses from the 28 facilities that were identified with TMEIC inverters. As to date:
  11 facilities have up to date firmware and recommended protection settings
  9 facilities have work scheduled to be complete by EOY
  7 facilities have consulted with TMEIC and are in progress of developing scope of work to be completed and timeline
  1 facility has not responded
ERCOT also followed up with all facilities with TMEIC inverters after Odessa 2021 event to ensure PLL Loss of Synch was disabled. 100% responded that the function was or had been disabled.
TMEIC notified ERCOT that all new projects will have the up-to-date firmware with overcurrent mitigation and recommended protection settings.

## Slide 5: Power Electronics Facilities Update
Issues identified in Power Electronic facilities were not as systemic as those with TMEIC inverters
Plant K/L has legacy inverters that continue to have ride-through performance issues
  ERCOT continued to work with RE after multiple events with similar ride-through performance issues
  RE has continued to attempt to improve performance for these events; appears to be limitations on the capability of these inverters
  Only facility in ERCOT with this inverter model
  RE has resubmitted models to reflect performance issues
Plant M also has older inverters and RE has adjusted LVRT and protection settings and facility has shown improved performance during subsequent events
  Only facility in ERCOT with this inverter model
  RE has resubmitted models
Plant Q had small number of inverters trip to AC overcurrent and high inverter temperature during Odessa 2022
  Unable to perform in depth root cause analysis due to inverter logs being overwritten during event
  Replaced SD cards with higher capacity to prevent logs from being overwritten during future events
  No model updates required
Plant S and Plant V had all inverters trip due to Vdc Bus Unbalance during Odessa 2022 event
  Power Electronics developed firmware update to improve DC side regulation and ride-through performance
  Firmware update implemented at both sites
  PE informed ERCOT DC side is not modeled in positive sequence nor EMT model; therefore, no model updates were required by REs

## Slide 6: Power Electronics Facilities Update

## Slide 7: Follow up with Other Facilities with Power Electronics Inverters
ERCOT sent out a Market Notice on May 26, 2023, instructing REs owning facilities with Power Electronics inverters to perform the following actions:
  Consult with Power Electronics to determine if the firmware upgrade to improve DC side regulation should be implemented at their facility or facilities
  If upgrade is needed, schedule a date with Power Electronics for the firmware upgrade to be implemented
  Notify ERCOT if the upgrade is needed with a timeline by June 30, 2023
There were 18 facilities identified by ERCOT that needed to verify if the upgrade was needed. As of date:
  16 facilities have responded that the firmware upgrade was either already implemented at their facility or has since been implemented
  ERCOT still waiting on confirmation from 2 facilities and follow up communication went out in Feb. 2024
Power Electronics notified ERCOT that all new projects will have the up-to-date firmware with DC side regulation implemented

## Slide 8: KACO Facilities Update
Issues with KACO facilities
  Poor logging capabilities preventing sufficient root cause analysis
  Improper voltage and frequency ride-through settings set directly on “No Trip” curve and not set based on equipment tolerances
  Inverter tripping due to AC overcurrent protection
  Lack of OEM support
Plant A involved in Odessa 2021 and not Odessa 2022. Root cause undetermined for 2021 event.
  Subsequent events have revealed improper ride-through settings and small number of inverters tripping due to AC overcurrent
  RE has recently identified not all inverters have identical settings. Changed RT settings of inverters that have tripped to match those that have successfully rode through and extended FRT and VRT settings
  Need to update models
Plant F continues to have ~40% of inverters trip during fault events due to AC overcurrent protection
  Extended FRT and VRT settings and improved inverter logging capabilities after Odessa events
  RE has not submitted updated models
Plant N/O has shown overall improved ride-through performance in recent events
  Extended FRT and VRT settings and improved inverter logging capabilities after Odessa events, also replaced PPC
  RE has resubmitted models which have been approved by ERCOT
  Facility had small number of inverters trip during recent event
Plant P has continued to have small number of inverters trip during recent events due to AC overcurrent protection
  RE has submitted PSSE and TSAT model, but not PSCAD

## Slide 9: KACO Facilities Update
ERCOT has not followed up with KACO facilities not involved in Odessa events:
  Lack of OEM support has made it difficult to determine actions needed for facilities that have not shown ride-through issues previously
  Only 4 additional facilities with KACO inverters exist in ERCOT that have not been involved in previous events

## Slide 10
Questions?