## Slide 1
2024 ERCOT UFLS Survey Overview and Timeline
Jake Pedigo
ERCOT Compliance Analyst
March 13, 2024

## Slide 2: NOGRR247: Change UFLS Stages and Load Relief Amounts
Partial Implementation Details of NOGRR247,
Change UFLS Stages and Load Relief Amounts
Nodal Operating Guide Revision Request (NOGRR) 247 modifies the ERCOT automatic Under-Frequency Load Shed (UFLS) program by increasing the number of Load shed stages from three to five and changing the Transmission Operator (TO) Load relief amounts to uniform increments of 5% for each stage. NOGRR247 also adds a UFLS minimum time delay of six cycles (0.1 seconds).
On March 11, 2024, Nodal Operating Guide language associated with NOGRR247 Change UFLS Stages and Load Relief Amounts, was partially implemented. This partial implementation increased the number of Load shed stages from three to five.
No earlier than October 1, 2026, Nodal Operating Guide language associated with NOGRR247 Change UFLS Stages and Load Relief Amounts will be fully implemented. This implementation will change the Transmission Operator (TO) Load relief amounts to uniform increments of 5% for each stage, add a UFLS minimum time delay of six cycles (0.1 seconds), and require utilization of supplemental anti-stall UFLS Stages.

## Slide 3: Survey Overview and Requirements
ERCOT ISO conducts the UFLS survey annually to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event.
ERCOT Nodal Operating Guides, 2.6.1 (1), Automatic Firm Load Shedding
At least 25% of the ERCOT System Load shall be equipped at all times with provisions for automatic Under-Frequency Load Shedding (UFLS) as described in this paragraph. In the event of an under-frequency event, each Transmission Operator (TO) shall provide Load relief by shedding the required percentage of its Distribution Service Provider (DSP)-connected Load and transmission-level Customer Load using automatic under-frequency relays, as specified in Table 1, Standard UFLS Stages, below. TOs may, but are not required to, provide supplemental anti-stall under-frequency Load relief in the amounts described in Table 2, Supplemental Anti-Stall UFLS Stages, below. If the TOs provide supplemental anti-stall under-frequency Load relief, the under-frequency relays shall be set to use the frequency thresholds and time delays described in Table 2. For the purposes of this paragraph, the TO Load will be the amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, when the ERCOT frequency drops to the 59.5 Hz threshold. As such, TO Load that has already been removed from the system without restoration prior to the 59.5 Hz frequency threshold will not apply to meeting TO Load relief percentage requirements as stated in Table 1 and Table 2 below.

## Slide 4: Survey Overview and Requirements
Table 1: Standard UFLS Stages
Table 2: Supplemental/Anti-Stall UFLS Stages
Frequency Threshold | TO Load Relief | Delay to Trip
59.5 Hz | At least 1.5% of the TO Load | 90 seconds
59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds
59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds
Frequency Threshold | TO Load Relief | Delay to Trip
59.3 Hz | At least 5% of the TO Load | No more than 30 cycles
59.1 Hz | A total of at least 5% of the TO Load | No more than 30 cycles
58.9 Hz | A total of at least 15% of the TO Load | No more than 30 cycles
58.7 Hz | A total of at least 15% of the TO Load | No more than 30 cycles
58.5 Hz | A total of at least 25% of the TO Load | No more than 30 cycles

## Slide 5: Survey Overview and Requirements
ERCOT Nodal Operating Guides 2.6.1 (3)
A TO may meet the Load relief requirements of the Supplemental anti-stall UFLS stages by utilizing Load that would otherwise be utilized to meet the 59.1 Hz, 58.9 Hz, 58.7 Hz, and 58.5 Hz standard UFLS stages. In this circumstance, the TO’s Load relief responsibility at the 59.1 Hz, 58.9 Hz, 58.7 Hz, and 58.5 Hz standard UFLS stages is reduced by the amount of Load already shed in the supplemental anti-stall UFLS stages. A TO may not meet the Load relief requirements of the supplemental anti-stall UFLS stages by utilizing Load that the TO needs to meet the 59.3 Hz standard UFLS stages.

## Slide 6: Survey Overview and Requirements
ERCOT Nodal Operating Guides 2.6.1 (2)
ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey. The TO shall identify those circuits armed with under-frequency relays, the corresponding amount of Load, and identify the frequency threshold. A TO shall not equip the entirety of its Load shed obligation in any one tier, and should endeavor to shed in controlled amounts that equal the difference between the TO Load relief required for each tier. If ERCOT identifies potential reliability issues related to distribution of Load shed across the tiers, ERCOT may require the TO to redistribute Load relief closer to the minimum amount required after submitting ERCOT’s proposal to redistribute Load relief to the TO and considering any comments submitted by the TO regarding the proposal. Compliance with this annual survey does not excuse the TO from compliance with the requirements of paragraph (1) above in an actual frequency event. To assist TOs, ERCOT will provide the TO’s inventory, including substation and capacity amounts, of registered Load Resources in its area within ten Business Days of receiving a request in writing from a TO.

## Slide 7: 2024 UFLS Survey Activity Timeline
Date | Activity
March 13th | Announcement of survey timeline to OWG.
March 28th | Market Notice sent to Authorized TO Representatives.
May 9th @ 11:00 AM | Date and time of survey.
July 12th | Survey results due to ERCOT.
August – September | Results reported to OWG, ROS, and TAC.