## Slide 1
Potential Price Corrections for Certain Days in January ‘24 – Incorrect Ratings Impacting the Real-Time and Day-Ahead Markets
Matthew Young
Supervisor, Market Validation
Technical Advisory Committee (TAC)
March 27, 2024

## Slide 2: Background
On January 29, 2024, ERCOT became aware of an issue concerning the ratings of certain transmission lines, series devices, and transformers. As part of the weekly model loads, the Energy Management System (EMS) retained outdated Normal/Emergency/15-Minute static ratings from the 2023 NOV_ML1 CIM model through the 2024 JAN_ML3 CIM model due to a defect in the EMS. The Real-Time Market (RTM) and Day-Ahead Market (DAM) use the static ratings from the EMS.
On January 30, 2024 around 23:00, ERCOT implemented a fix to ensure that correct static ratings for the transmission lines, series devices, and transformers are used in EMS from the CIM models.
Market Notice M-A020524-01 was issued on February 5, 2024, notifying the market of the issue and ERCOT’s intent, upon completion of impact analysis, to seek ERCOT Board of Directors (Board) approval for price correction as specified by ERCOT Protocol Sections 4.5.3(6)(b) and 6.3(7)(b) for the DAM and RTM, respectively.
Market Notice M-A020524-02 was issued on March 12, 2024, notifying the market of the price impact results and ERCOT’s intent to seek Board review.

## Slide 3: RTM Impact Analysis
ERCOT Protocols Section 6.3(7)(b) requires that the absolute value impact to any single Counter-Party (CP) meet one of the following two criteria before seeking approval from the Board.
  2% and also greater than $20,000; or
  20% and also greater than $2,000.
ERCOT determined that there were three ODs that met criteria for significance for the RTM.
Operating Day | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(i) | Counter-Parties meeting criteria in Protocol Section 6.3(7)(b)(ii)
1/15/2024 | 38 | 26
1/17/2024 | 38 | 69
1/19/2024 | 8 | 16

## Slide 4: RTM Impact Analysis
For each OD that met the criteria for RTM, the table below has the maximum estimated absolute value impact to Counter-Parties:
Operating Day | Maximum Amount ($Thousands) | Maximum Percentage for Criteria (i)* | Maximum Percentage for Criteria (ii)**
1/15/2023 | $883.26 | 172.03% | 172.03%
1/17/2023 | $1051.09 | 262.75% | 565.49%
1/19/2023 | $160.74 | 185.00% | 185.00%
* The maximum of percentage change to any single Counter-Party with impact more than $20,000 (set as NA when no single Counter-Party has impact more than $20,000)
** The maximum of percentage change to any single Counter-Party with impact more than $2,000 (set as NA when no single Counter-Party has impact more than $2,000)

## Slide 5: RTM Impact Analysis
For each OD that met the criteria for RTM, the table below has the maximum estimated change in charges due to ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges. The percent amount is the absolute value of the percent impact to the previously settlement net amount due to/from ERCOT.
Operating Day | Change in Statement Charges Due to ERCOT ($ thousands) | 
1/15/2023 | $0.44 | 0.00061%
1/17/2023 | $(877.02) | 3.84%
1/19/2023 | $66.54 | 0.52%

## Slide 6: DAM Impact Analysis
ERCOT Protocols Section 4.5.3(6)(b) requires that the absolute value impact to any single Counter-Party (CP) meet one of the following two criteria before seeking approval from the Board.
  2% and also greater than $20,000; or
  20% and also greater than $2,000.
ERCOT determined that there were three ODs that met criteria for significance for the DAM.
Operating Day | Counter-Parties meeting criteria in Protocol Section 4.5.3(6)(b)(i) | Counter-Parties meeting criteria in Protocol Section 4.5.3(6)(b)(ii)
1/10/2024 | 5 | 7
1/15/2024 | 1 | 0
1/17/2024 | 6 | 8
1/18/2024 | 6 | 41
1/19/2024 | 6 | 18
1/20/2024 | 0 | 2
1/23/2024 | 0 | 1
1/25/2024 | 0 | 1

## Slide 7: DAM Impact Analysis
For each OD that met the criteria for DAM, the table below has the maximum estimated absolute value impact to Counter-Parties:
* The maximum of percentage change to any single Counter-Party with impact more than $20,000 (set as NA when no single Counter-Party has impact more than $20,000)
** The maximum of percentage change to any single Counter-Party with impact more than $2,000 (set as NA when no single Counter-Party has impact more than $2,000)
Operating Day | Maximum Amount ($Thousands) | Maximum Percentage for Criteria (i)* | Maximum Percentage for Criteria (ii)**
1/10/2024 | $121.85 | 47.94% | 183.71%
1/15/2024 | $21.85 | 12.48% | NA
1/17/2024 | $41.49 | 42.82% | 1276.81%
1/18/2024 | $59.17 | 447.50% | 1281.96%
1/19/2024 | $249.24 | 67.04% | 120.64%
1/20/2024 | $2.08 | NA | 61.45%
1/23/2024 | $2.49 | NA | 23.25%
1/25/2024 | $2.47 | NA | 89.72%

## Slide 8: DAM Impact Analysis
For each OD that met the criteria for DAM, the table below has the maximum estimated change in charges due to ERCOT. Negative amounts are increased payments to Market Participants; positive amounts are increased charges. The percent amount is the absolute value of the percent impact to the previously settlement net amount due to/from ERCOT.
Operating Day | Change in Statement Charges Due to ERCOT ($ thousands) | 
1/10/2024 | $(219.91) | 2.29%
1/15/2024 | $(19.99) | 0.02%
1/17/2024 | $(204.60) | 0.59%
1/18/2024 | $(495.81) | 5.68%
1/19/2024 | $(691.26) | 6.27%
1/20/2024 | $(12.85) | 0.10%
1/23/2024 | $16.47 | 0.14%
1/25/2024 | $40.40 | 0.52%

## Slide 9: Next Steps
ERCOT intends to seek an approval of correction to DAM and RTM prices for the impacted ODs that met the necessary criteria at the Reliability and Market Committee meeting on April 22, 2024, and the Board meeting on April 23, 2024.