## Slide 1
NOGRR 245
TAC
Stephen Solis – Principal, System Operations Improvement
March 27th, 2024

## Slide 2: Overview
NOGRR 245 originally proposed to enhance clarity and specificity of IBR ride through requirements and align w/ most relevant parts of IEEE 2800-2022 and NERC Reliability Guidelines
ROS approved a NOGRR 245 version on 9/14/23 that harms reliability
FERC Order 901:
  Directs NERC to address same risks NOGRR245 addresses
  Clarified need for retroactive applicability w/ limited technical exemptions for legacy IBRs for voltage ride-through requirements (planners/operators must address risk caused by exemptions)
ERCOT submitted comments on 1/8/24 to respond to new direction
  Joint commenters still opposed ERCOT comments
ERCOT has worked w/ joint commenters and made significant concessions in an attempt to address their concerns
ERCOT proposes to bifurcate the most challenging technical issues to a future NOGRR
Issues remain because ERCOT cannot concede any further without significant risk to ERCOT System reliability

## Slide 3: Outstanding Issues
Effective Date for new requirements
  ERCOT originally proposed having new (IEEE 2800-2022) requirements apply to IBRs after 1/1/23
    Now proposes 6/1/23
    Moving that date to NOGRR approval date likely exempts 20-30 GWs of IBRs from new requirements
  ERCOT proposes exemptions and extensions to phase in new requirements
Joint Commenters propose essentially no enforcement ride-through requirements on legacy IBRs
  ERCOT wants “floor” to be the current ride-through requirements (e.g. NOG § 2.9(2))
Fault disturbance ride-through requirement (vs. non-fault)
  Consistent with P2800-2 drafting team, ERCOT maintains the current requirements that IBRs/WGRs must ride through faults and not trip due to unreliable measurements of phase angle or RoCoF
ERCOT proposes that limitations causing reliability issues may result in Resource disconnection until the reliability issue is resolved

## Slide 4: ERCOT Proposed Changes NOGRR 245 (3/19/24)
Limited technical exemptions for legacy IBRs with SGIA before 6/1/23
  Must maximize capability through parameterization, settings changes, software upgrades and commercially reasonable hardware upgrade kits
  RE must accurately represent technical limitations in all models provided to ERCOT
  Must meet latest requirements upon reinvestment (e.g., repower/retrofit requiring GIM process)
  Must annually determine if modifications are available and “commercially reasonable”
  ERCOT will exercise discretion in approving exemptions with “guardrails” in place
  ERCOT expects (best information available) its language will result in:
    2 – 4 GW limited technical exemptions out of 16 GW of WGRs with SGIA prior to 1/16/14
    < 1 GW limited technical exemptions out of remaining >50 GWs of IBRS with SGIA after 1/16/14
ERCOT proposes deferring technically complex requirements to future NOGRR
  Expectations for RoCoF and Phase Angle Jump remain at status quo
    If voltage or frequency are within “no trip” zones, IBR must ride through (NOG § 2.9(2))
    Aligns with P2800-2: during fault events, frequency and phase angle measurements are not reliable and the IBR (both new and legacy) should not trip for these parameters
  Removed multiple excursion requirements for legacy IBRs for now (IEEE 2800 for new)
  Future NPRR/NOGRR will address SSR/control response timing, phase angle jump, RoCoF, and multiple excursions; additional technical discussions needed
    Better understanding/consistency in how RoCoF and PAJ are calculated/protected to properly set performance requirements for fault conditions (IEEE 2800 identifies IBR capability requirement for non-fault conditions)
    Requirement depends on time frame of calculation
    TSPs to evaluate reclose schemes for IBRs
    Additional discussion to address energy dissipation during multiple excursions

## Slide 5: ERCOT Proposed Changes NOGRR 245 (3/19/24)
Included “Commercially Reasonable Efforts” Section
  Limited technical exemptions may be allowed if technically feasible improvements are not commercially reasonable
  RE must mitigate performance failure
  PUCT will determine extent to which IBR or WGR must mitigate performance failure
Removed language re: operational restrictions for performance failures
  ERCOT already has authority to take actions to ensure ERCOT System reliability
Aligned report dates at request of Joint Commenters to not overlap w/ winterization reports
Modified Tables A and B in 2.9.1.1(1) to ensure no reduction of VRT requirements for new IBRs
Added language describing processes for exemptions, extensions and appeals
  More consistency
  Appeals are faster than ADR process

## Slide 6: Additional Comments on ERCOT proposal
ERCOT set 6/1/23 SGIA date to make new IBRs subject to §2.9.1.1 and IEEE 2800 because:
  ERCOT has been telling IBR owners of upcoming IEEE 2800 requirements since early 2022
  Initial proposed date was 1/1/23; delaying to 6/1/23 results in ~ 6 GW of IBRs not having to meet new requirements
  Delay to 6/1/24 (per Joint Commenters) results in additional 20 - 30 GWs not required to meet new requirements
  >66 GW of legacy IBRs would not have to meet higher requirements
  Language accommodates reasonable “phased in” approach for all IBRs with SGIA after 6/1/23
    IBR w/ COD before 12/31/26 (moved from 6/1/26) can request limited technical exemption for portions it cannot meet
    IBR w/ COD after 12/31/26 can request limited extension up to 12/31/28 to fully comply
ERCOT included “Commercially Reasonable Efforts” because Joint Commenters insisted on it and to incentivize REs to quickly implement easier, less costly changes
  However, ERCOT does not support “commercially reasonable” concept because:
    Removing significant reliability risk IBR and WGR ride-through performance failures pose to grid should outweigh commercial considerations
    Lack of firm requirements does not incentivize OEMs to develop solutions to improve ride-through performance
    “Innocent bystander” stakeholders bear burden of paying for transmission upgrades, congestion charges, potential blackouts and equipment impacts to accommodate IBR owners
  RE must mitigate a performance failure to applicable requirements
  PUCT will determine extent to which IBR/WGR must mitigate performance failure

## Slide 7: Reliability Impact of ERCOT-Proposed Exemptions
Can move forward w/ OEM-identified parameterization and commercially reasonable upgrade kits owners are waiting to authorize and procure
Allows NOGRR 245 to progress by bifurcating technically-complex parameters requiring additional discussion (SSR, PAJ, RoCoF, multiple excursions)
Allows a feasible path forward for IBRs w/ SGIA beyond 6/1/23 with challenges to immediately meeting IEEE 2800 requirements
Reliability risk continues due to IBRs w/ exemptions
Modeled limitations may impact stability limits
  ERCOT may update or add Generic Transmission Limits (GTLs) as needed
  Impact of exceeding some GTLs may make them an IROL
  May need to implement additional transmission projects
Some newly-modeled limitations and repeated performance failures may require new credible contingencies (e.g., combined transmission/generator contingency) in operations and planning
  May result in additional transmission congestion
  May create new voltage, cascading or instability conditions
Key Takeaway: Proposed exemptions should help faster adoption of commercially reasonable improvements and IEEE 2800 but at expense of continued reliability risk and associated impacts

## Slide 8: Additional assumptions
IBR performance requirements are one part of overall solution to address risk
  IBR performance requirements (NOGRR 245) w/ appropriate enforcement
  System strength upgrades (e.g., 6 new synchronous condensers)
  Grid Forming capability adoption
  Modeling and testing improvements (DWG/IBRWG collaboration)
  Disturbance monitoring equipment installs (NOGRR 255)
  Potential planning criteria adjustments
To offset risk, exemptions must be accompanied by:
  Clear expectations re: operating restrictions for failures posing reliability risk
  Models and contingencies accurately reflect limitations
  Proper active/reactive power controls coordination
The actions required to offset risk could lead to additional operation and planning impacts such as congestion and system improvements
Key Takeaway: Proposal assumes willingness to accept more reliability risk, adopting other risk offset activities, and other system cost impacts are acceptable to impacted entities

## Slide 9: Updated timeline for NOGRR 245 (i.e. Next steps)

## Slide 10: NOGRR 245 – ERCOT Recommendation
ERCOT strongly recommends TAC adopt ERCOT 3/19/24 comments
ERCOT has serious concerns w/ “commercially reasonable” concept as prioritizing one market segment’s commercial interests over societal risk of uncontrolled loss of ERCOT System; however, continued delays to implementing NOGRR 245 will continue exposing ERCOT System to unacceptable level of risk
ERCOT continues recommending entities maximize ride-through capabilities w/o delay to minimize reliability risk to ERCOT System
Additional rule changes needed to address more complex technical rules around SSR, phase angle jump, RoCoF, multiple excursions
Key Takeaway: ERCOT strongly recommends approval of NOGRR 245 with ERCOT 3/19/24 comments despite its concerns w/ concessions because further delay continues to escalate risk to ERCOT System or may be too late

## Slide 11
Questions?