## Slide 1
PDCWG Report to ROS
Chair: Kevin Bunch, EDF Trading North America
Vice Chair: Chad Mulholland, NRG
ROS
April 4th, 2024

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    Analysis of Disturbances/Frequency Events
    Follow up Discussion: RRS-PFR Limits
    ERCOT Frequency Control Metrics and Regulation Reports
    Business Practice Manual Update; ESRs Telemetry
    TRE Report – Revisit a draft SAR regarding ESRs in BAL-001
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of February
      39 Units failed Initial Response and 37 failed Sustained Response
      7 Units failed carrying RRS
  Frequency Control Report

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 395 MW/0.1 Hz
IMFR Performance currently
1251.68 MW/0.1HZ

## Slide 5
Questions?

## Slide 6: Frequency Control Report
February 2024

## Slide 7: CPS1 Performance

## Slide 8: RMS1 Performance of ERCOT Frequency
Notes: 15.19 mHz on avg for February 2024

## Slide 9: Frequency Profile Analysis

## Slide 10: Time Error Corrections

## Slide 11: ERCOT Total Energy
Notes: 30,761,552 MWh

## Slide 12: ERCOT Total Energy from Wind Generation
Notes:   10,944,115 MWH

## Slide 13: ERCOT % Energy from Wind Generation
Notes: 35.58% of total energy was provided by wind generation

## Slide 14: ERCOT Total Energy from Solar Generation
Notes: 2,646,220 MWh

## Slide 15: ERCOT % Energy from Solar Generation
Notes: 8.60% of total energy was provided by solar generation

## Slide 16: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in February 2024 = 145,331 MW*s on 2/25/2024
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
Data:
Mean: 173,614 MW*s
Max: 241,450 MW*s on February 29th
Min: 145,331 MW*s on February 25th

## Slide 17: ERCOT Inertia Trend
Notes: Summary of ERCOT intertia for the previous 10 years. Lowest inertia this year was on February 25th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.