## Slide 1
Large Load Revision Requests
Current Status and Proposed Next Steps
NPRR1191, PGRR111, NOGRR256

## Slide 2: Current status of NPRR1191 and related Revision Requests
ERCOT filled NPRR1191 and related Revision Requests on 8/1/2023.
Since then, comments have been filed by multiple stakeholders and ERCOT has held 6 meetings of the LFLTF to discuss concerns.
Stakeholders are at an impasse on several important topics.
ERCOT proposes the following steps to move forward in areas where there is consensus and mitigate the reliability risks on topics where there is not.

## Slide 3: Proposed Next Steps – Large Load Interconnection Process
Original Concept
Establish a formal interconnection process for Large Loads connecting in ≤ 24 months. The customer would submit a project in RIOO and interface with both ERCOT and the TSP.
Proposed Next Steps
Establish a formal interconnection process for all Large Loads that is closer to the current interim process. The TSP (and RE, if applicable) will interface with ERCOT on the customer’s behalf.

## Slide 4: Proposed Next Steps – Registration of Loads 25 MW and Greater
Original Concept
Require loads 25 MW and greater to register with ERCOT and provide data on equipment and end use.
Proposed Next Steps
Require TSPs to submit additional modeling data needed to identify loads 25 MW and greater.

## Slide 5: Proposed Next Steps – Ramp Rate Restrictions
Original Concept
Restrict the ramp rate of Large Loads that are not registered with ERCOT as a CLR.
Proposed Next Steps
Do not impose ramp rate restrictions at this time to allow for more study and discussion of the issue.
Large Load ramping behavior will be reflected in AS requirements.
Create a periodic report to TAC on this issue.

## Slide 6: Proposed Next Steps – Voltage Ride Through
Original Concept
Require Large Loads to ride through voltage disturbances depending on severity and duration.
Proposed Next Steps
Do not impose Voltage Ride Through requirements at this time to allow for more study and discussion of the issue.
Require TSPs to submit and validate facility-specific dynamic models for Large Loads.
Immediately develop a standard defining permissible amount of load tripping for any single contingency and file a PGRR requiring TSPs to build upgrades to mitigate.

## Slide 7: Proposed Next Steps – Registered Curtailable Load (RCLs)
Original Concept
Create a new Registered Curtailable Load (RCL) category that can be shed by ERCOT prior to EEA.
Proposed Next Steps
Do not create a RCL category at this time (no incentive to sign up).

## Slide 8: Impact to NPRR1191 and related Revision Requests
 | Topic | ERCOT Action
1 | Large Load Interconnection Process | File comments on NPRR1191 and PGRR111 to modify the proposed interconnection process
2 | Registration of Loads ≥ 25 MW | File comments on NPRR1191 and PGRR111 to shift the obligation to provide Large Load data to ERCOT from the customer to TSPs
3 | Ramp Rate Restrictions | File comments to remove ramp rate restriction language from NPRR1191
4 | Voltage Ride Through Requirements | Withdraw NOGRR256 and develop an additional new PGRR
5 | Registered Curtailable Load | File comments removing RCLs from NPRR1191 and withdraw NOGRR256
To implement the concepts detailed in this presentation, ERCOT will take the following actions on NPRR1191 and related Revision Requests: