## Slide 1
Generation Resource Energy and Regulation Deployment Performance Report for March 2024

## Slide 2: Non-IRR GREDP < 85% – March 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 451 | 1 | 2 | 0.67 | 50.00
Unit 452 | 1 | 2 | 0.67 | 50.00
Unit 454 | 0 | 1 | 0.47 | 0.00

## Slide 3: IRR Summary – March 2024
IRR | Fleet | < 95% | > 100 INT, < 95%
GREDP Average (%) | 83.20 | 75.42 | 80.85
GREDP Median (%) | 91.13 | 83.52 | 86.74
Average MW Error | 6.13 | 6.40 | 6.87
Median MW Error | 5.50 | 5.66 | 6.03
Total Intervals Scored | 149,053 | 80,087 | 77,596
100+ Intervals Scored | 170 | 190 | 120.00
Total Intervals Scored Average | 409.49 | 388.77 | 646.63

## Slide 4: IRR ≥ 95%, ≥ 100 Scored Intervals – March 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 2 | 3,081 | 3,094 | 8.40 | 99.58
Unit 4 | 2,821 | 2,941 | 8.16 | 95.92
Unit 5 | 2,766 | 2,900 | 8.10 | 95.38
Unit 6 | 2,880 | 2,883 | 4.38 | 99.90
Unit 7 | 2,837 | 2,860 | 4.90 | 99.20
Unit 10 | 2,640 | 2,674 | 10.90 | 98.73
Unit 11 | 2,512 | 2,549 | 3.60 | 98.55
Unit 12 | 2,515 | 2,520 | 2.37 | 99.80
Unit 13 | 2,456 | 2,473 | 2.76 | 99.31
Unit 14 | 2,416 | 2,440 | 3.97 | 99.02
Unit 15 | 2,244 | 2,303 | 4.04 | 97.44
Unit 16 | 2,060 | 2,081 | 2.97 | 98.99
Unit 19 | 1,902 | 1,929 | 2.33 | 98.60
Unit 20 | 1,871 | 1,897 | 4.25 | 98.63
Unit 21 | 1,840 | 1,894 | 3.26 | 97.15
Unit 22 | 1,797 | 1,885 | 5.59 | 95.33
Unit 23 | 1,842 | 1,854 | 4.38 | 99.35
Unit 25 | 1,755 | 1,771 | 4.39 | 99.10
Unit 27 | 1,689 | 1,764 | 2.43 | 95.75

## Slide 5: IRR ≥ 95%, ≥ 100 Scored Intervals – March 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 28 | 1,749 | 1,760 | 10.16 | 99.38
Unit 33 | 1,463 | 1,504 | 7.40 | 97.27
Unit 37 | 1,366 | 1,405 | 9.29 | 97.22
Unit 38 | 1,321 | 1,370 | 2.95 | 96.42
Unit 39 | 1,257 | 1,303 | 1.51 | 96.47
Unit 40 | 1,254 | 1,273 | 4.22 | 98.51
Unit 42 | 1,167 | 1,202 | 7.05 | 97.09
Unit 43 | 1,175 | 1,200 | 2.64 | 97.92
Unit 47 | 1,043 | 1,054 | 8.23 | 98.96
Unit 51 | 977 | 992 | 1.22 | 98.49
Unit 55 | 886 | 927 | 21.89 | 95.58
Unit 57 | 861 | 901 | 7.28 | 95.56
Unit 59 | 854 | 870 | 5.80 | 98.16
Unit 65 | 806 | 825 | 7.76 | 97.70
Unit 66 | 789 | 824 | 5.76 | 95.75
Unit 70 | 758 | 783 | 11.27 | 96.81
Unit 71 | 755 | 781 | 4.58 | 96.67
Unit 73 | 741 | 769 | 1.92 | 96.36
Unit 77 | 735 | 743 | 6.72 | 98.92

## Slide 6: IRR ≥ 95%, ≥ 100 Scored Intervals – March 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 80 | 634 | 658 | 12.08 | 96.35
Unit 95 | 431 | 446 | 8.11 | 96.64
Unit 105 | 328 | 344 | 2.49 | 95.35
Unit 112 | 301 | 301 | 4.92 | 100.00
Unit 113 | 282 | 295 | 5.76 | 95.59
Unit 151 | 153 | 161 | 5.93 | 95.03
Unit 157 | 134 | 135 | 3.46 | 99.26
Unit 159 | 127 | 133 | 10.15 | 95.49
Unit 161 | 119 | 125 | 4.25 | 95.20
Unit 162 | 118 | 124 | 1.37 | 95.16
Unit 164 | 117 | 121 | 5.70 | 96.69
Unit 168 | 103 | 105 | 3.39 | 98.10

## Slide 7: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 1 | 3,434 | 3,696 | 6.64 | 92.91
Unit 3 | 2,514 | 2,964 | 6.33 | 84.82
Unit 8 | 2,389 | 2,839 | 3.91 | 84.15
Unit 9 | 2,563 | 2,794 | 5.74 | 91.73
Unit 17 | 1,767 | 1,979 | 5.10 | 89.29
Unit 18 | 1,842 | 1,961 | 4.83 | 93.93
Unit 24 | 1,673 | 1,795 | 2.80 | 93.20
Unit 26 | 1,460 | 1,770 | 5.05 | 82.49
Unit 29 | 1,616 | 1,753 | 2.97 | 92.18
Unit 30 | 1,615 | 1,753 | 4.23 | 92.13
Unit 31 | 1,378 | 1,651 | 2.35 | 83.46
Unit 32 | 1,391 | 1,554 | 9.10 | 89.51
Unit 34 | 1,409 | 1,488 | 8.80 | 94.69
Unit 35 | 1,271 | 1,466 | 2.07 | 86.70
Unit 36 | 1,169 | 1,461 | 5.79 | 80.01
Unit 41 | 815 | 1,259 | 9.82 | 64.73
Unit 44 | 1,120 | 1,197 | 4.53 | 93.57
Unit 45 | 1,052 | 1,155 | 4.46 | 91.08
Unit 46 | 1,074 | 1,132 | 7.07 | 94.88

## Slide 8: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 48 | 950 | 1,049 | 5.69 | 90.56
Unit 49 | 972 | 1,045 | 3.77 | 93.01
Unit 50 | 982 | 1,045 | 6.01 | 93.97
Unit 52 | 793 | 990 | 6.99 | 80.10
Unit 53 | 882 | 985 | 4.64 | 89.54
Unit 54 | 891 | 961 | 8.18 | 92.72
Unit 56 | 741 | 922 | 6.24 | 80.37
Unit 58 | 789 | 894 | 3.73 | 88.26
Unit 60 | 770 | 861 | 11.19 | 89.43
Unit 61 | 809 | 852 | 8.49 | 94.95
Unit 62 | 795 | 847 | 6.11 | 93.86
Unit 63 | 395 | 842 | 4.84 | 46.91
Unit 64 | 770 | 836 | 10.06 | 92.11
Unit 67 | 559 | 802 | 7.47 | 69.70
Unit 68 | 548 | 797 | 1.19 | 68.76
Unit 69 | 489 | 789 | 9.03 | 61.98
Unit 72 | 717 | 779 | 17.17 | 92.04
Unit 74 | 641 | 767 | 4.29 | 83.57
Unit 75 | 631 | 759 | 6.94 | 83.14

## Slide 9: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 76 | 674 | 758 | 5.08 | 88.92
Unit 78 | 611 | 692 | 5.54 | 88.29
Unit 79 | 580 | 667 | 7.17 | 86.96
Unit 81 | 359 | 654 | 3.90 | 54.89
Unit 82 | 612 | 652 | 9.32 | 93.87
Unit 83 | 561 | 626 | 6.22 | 89.62
Unit 84 | 392 | 609 | 6.16 | 64.37
Unit 85 | 554 | 597 | 10.73 | 92.80
Unit 86 | 522 | 558 | 12.97 | 93.55
Unit 87 | 443 | 542 | 4.85 | 81.73
Unit 88 | 485 | 536 | 5.21 | 90.49
Unit 89 | 323 | 532 | 1.79 | 60.71
Unit 90 | 368 | 501 | 2.61 | 73.45
Unit 91 | 378 | 483 | 2.24 | 78.26
Unit 92 | 452 | 476 | 2.48 | 94.96
Unit 93 | 360 | 460 | 2.25 | 78.26
Unit 94 | 388 | 456 | 8.68 | 85.09
Unit 96 | 284 | 425 | 4.80 | 66.82
Unit 97 | 358 | 402 | 2.50 | 89.05

## Slide 10: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 98 | 370 | 398 | 7.57 | 92.96
Unit 99 | 364 | 393 | 10.05 | 92.62
Unit 100 | 363 | 386 | 1.04 | 94.04
Unit 101 | 218 | 372 | 4.65 | 58.60
Unit 102 | 333 | 356 | 2.82 | 93.54
Unit 103 | 334 | 353 | 6.90 | 94.62
Unit 104 | 202 | 353 | 18.28 | 57.22
Unit 106 | 178 | 343 | 12.81 | 51.90
Unit 107 | 267 | 341 | 14.05 | 78.30
Unit 108 | 301 | 338 | 3.99 | 89.05
Unit 109 | 201 | 337 | 7.53 | 59.64
Unit 110 | 269 | 336 | 11.19 | 80.06
Unit 111 | 269 | 310 | 3.11 | 86.77
Unit 114 | 251 | 292 | 19.97 | 85.96
Unit 115 | 270 | 291 | 4.76 | 92.78
Unit 116 | 189 | 287 | 10.14 | 65.85
Unit 117 | 112 | 287 | 8.16 | 39.02
Unit 118 | 252 | 278 | 8.61 | 90.65
Unit 119 | 261 | 275 | 4.23 | 94.91

## Slide 11: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 120 | 251 | 275 | 3.26 | 91.27
Unit 121 | 93 | 269 | 10.73 | 34.57
Unit 122 | 230 | 265 | 8.94 | 86.79
Unit 123 | 117 | 263 | 14.47 | 44.49
Unit 124 | 117 | 261 | 10.77 | 44.83
Unit 125 | 220 | 259 | 6.81 | 84.94
Unit 126 | 238 | 251 | 6.30 | 94.82
Unit 127 | 186 | 249 | 7.07 | 74.70
Unit 128 | 204 | 244 | 10.84 | 83.61
Unit 129 | 129 | 224 | 12.86 | 57.59
Unit 130 | 182 | 216 | 6.21 | 84.26
Unit 131 | 146 | 213 | 3.64 | 68.54
Unit 132 | 197 | 210 | 1.91 | 93.81
Unit 133 | 166 | 210 | 8.09 | 79.05
Unit 134 | 197 | 210 | 3.19 | 93.81
Unit 135 | 170 | 210 | 3.52 | 80.95
Unit 136 | 65 | 208 | 9.80 | 31.25
Unit 137 | 191 | 205 | 12.00 | 93.17
Unit 138 | 175 | 200 | 3.93 | 87.50

## Slide 12: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 139 | 158 | 199 | 4.56 | 79.40
Unit 140 | 168 | 180 | 15.57 | 93.33
Unit 141 | 155 | 176 | 6.05 | 88.07
Unit 142 | 148 | 175 | 18.17 | 84.57
Unit 143 | 160 | 172 | 9.69 | 93.02
Unit 144 | 126 | 171 | 5.10 | 73.68
Unit 145 | 135 | 171 | 11.08 | 78.95
Unit 146 | 149 | 164 | 4.35 | 90.85
Unit 147 | 152 | 164 | 17.09 | 92.68
Unit 148 | 139 | 163 | 5.41 | 85.28
Unit 149 | 119 | 162 | 7.77 | 73.46
Unit 150 | 100 | 161 | 9.83 | 62.11
Unit 152 | 147 | 157 | 2.08 | 93.63
Unit 153 | 27 | 157 | 10.55 | 17.20
Unit 154 | 104 | 139 | 5.05 | 74.82
Unit 155 | 112 | 137 | 3.01 | 81.75
Unit 156 | 120 | 135 | 13.01 | 88.89
Unit 158 | 126 | 134 | 1.44 | 94.03
Unit 160 | 78 | 128 | 3.41 | 60.94

## Slide 13: IRR < 95%, ≥ 100 Scored Intervals – February 2024
Unit | Total Intervals Passed | Total Intervals Scored | Std. Dev. (ATG - Exp MW) | GREDP Monthly Score
Unit 163 | 111 | 123 | 2.56 | 90.24
Unit 165 | 78 | 117 | 4.86 | 66.67
Unit 166 | 95 | 113 | 5.62 | 84.07
Unit 167 | 101 | 108 | 1.96 | 93.52
Unit 169 | 79 | 104 | 8.17 | 75.96
Unit 170 | 66 | 103 | 5.36 | 64.08