## Slide 1
ECRS Methodology for 2024 And Deployment Triggers
TAC
April 15, 2024
Nitika Mago
Balancing Operations Planning

## Slide 2: Introduction
As part of the 2024 Ancillary Service (AS) Methodology discussion at the Technical Advisory Committee (TAC) and ERCOT Board (BoD), ERCOT was asked to review by April 30, 2024 the methodology used to compute ERCOT Contingency Reserve Service (ECRS) and potential alternate solutions, taking into account the analysis that the Independent Market Monitor (IMM) has conducted on the impact of ECRS.
ERCOT has worked with the IMM on this item.
This slide deck will be responsive to the TAC request and will also share ERCOT’s thoughts on how the AS Methodology could evolve in the future to efficiently account for the operational risks and reliability needs.
Ongoing/Upcoming Ancillary Service Initiatives
Consider changes to AS for 2025, including PUC to approve AS Methodology
AS Study for Legislature (PUC/IMM/ERCOT)
Effective January 2025
Effective Beyond 2025
Due October 2024
Due September 2024
Consider changes to ECRS before Summer 2024 (TAC Request)
Effective
??
Due April 2024

## Slide 3: 2024 ECRS Methodology Review
Taking into consideration the study tools that are used today, the growing nature of the operating risks for which ECRS is required, and analysis conducted, ERCOT is not supportive of any further changes in the ECRS methodology for 2024. ERCOT notes that for 2024 several changes have already been made to the ECRS methodology as a part of last year’s review. These changes resulted in reducing 2024 ECRS quantities, on an average by 442 MW in each hour (~21% reduction).
Background on Studies/Tools
As installed capacities for wind and solar increase, ERCOT’s net load uncertainty and variability are also growing.
Prior to the operating hour, ERCOT relies on Reliability Unit Commitment (RUC)* (hourly resolution) to ensure sufficient capacity is committed for every hour. ERCOT uses hourly wind, solar and load forecasts in RUC – these essentially represent the average net load forecasted each hour and do not capture the variability in net load within the hour.
Within the operating hour, ERCOT relies on Security Constrained Economic Dispatch (SCED) (5-min resolution) to dispatch resources. ERCOT uses a 5-min wind, solar and load forecasts in SCED - these essentially represent the average net load forecasted each 5-min interval.
ERCOT relies on Regulation to cover any uncertainty in the 5-min net load forecasts used by SCED.
*It is worth noting that the current RUC software does not have a ramping constraint, so it doesn’t take ramping into account when committing resources.

## Slide 4: 2024 ECRS Methodology Review, Contd.
Reliability Considerations (Slide 8 has a graphic to visualize the scenario discussed below)
With growth in solar and increasing intra-hour variability in net load, there can be times when the ramping capacity of online resources is not sufficient to cover the 10-min out net load ramps.
These situations typically arise, when a weather-front moves through the region sooner or later than predicted.
During some of these event, the under forecast in net load can persist for several SCED-intervals; AND the next offline unit that can help alleviate the capacity needs is typically an offline Non-Spin unit.
Under such situations, ECRS is one of the tools the Control Room may rely on to operate reliably till the offline Non-Spin unit can be brought online.
Per protocols upon deployment offline Non-Spin units may take up to 30 minutes to be On-Line. ERCOT has evaluated the cold start times of units that provided offline Non-Spin in 2023 at a 5-min resolution and confirmed that units that were carrying offline Non-Spin even during the peak hours had a cold start up time of up to 30 minutes. (See Slide 9)
  ERCOT will evaluate trends in offline Non-Spin provision further during the 2025 AS Methodology review.

## Slide 5: Deployment of SCED Dispatchable ECRS
ERCOT has reviewed the deployment approach for SCED Dispatchable ECRS with the IMM.
ERCOT agrees with IMM’s recommendation that similar to online Non-Spin, some portion of SCED Dispatchable ECRS in every hour can be released at an Energy offer floor as part of a standing deployment instruction within the protocols.
  This concept may need some system changes (potentially both for systems in ERCOT and at Market Participant end), this option may not be feasible to fully implement by Summer 2024.
  ERCOT is targeting to submit an NPRR for “Standing ECRS Deployment” concept for the June Protocol Revision Subcommittee (PRS) meeting.
Absent the “Standing ECRS Deployment” concept, another mechanism to alleviate some of IMM’s concerns if conditions like last Summer to reoccur, could be by releasing some SCED Dispatchable ECRS earlier than when it was historically.
  Hence NPRR1224, ECRS Manual Deployment Triggers, was submitted to add a new trigger based on Power Balance Penalty Curve violation (developed from options IMM provided) to manually release SCED dispatchable ECRS.
However, PRS has tabled NPRR 1224 at its April meeting, making a decision on NPRR1224 unlikely before mid-summer. Without this guidance on an appropriately-balanced ECRS deployment trigger, this Summer, ERCOT intends to release ECRS in a similar manner to last year until such guidance is received.

## Slide 6: Summary & Thoughts on Future
With increase in the installed capacities for wind and solar, ERCOT’s net load uncertainty and variability have grown. Further, with the way the ERCOT grid is expected to evolve in the near future, the net load uncertainty and variability will continue to grow/evolve as well. The difference between AS quantity needed for reliable operations for a typical condition and for worst-case or near worst-case conditions will be much greater.
A holistic review of the entire AS Methodology may soon be necessary to ensure that this procedure is able to appropriately account the probabilistic risk that impact reliability for a typical day from a non-typical day while appropriately take into the account the prevailing reliability operating practices.
  In this regards, ERCOT considers the AS study for legislature a good avenue to start this discussion but given its timeline it may not be the sole avenue for such a discussion.
In ERCOT’s opinion some of the IMM’s concerns related to ECRS methodology may also be better addressed as a part of this holistic review.
ERCOT considers NPRR1224 and the future NPRR on “Standing ECRS Deployment” to be a step that should provide some incremental improvements while work on the boarder issues continues.
ERCOT looks forward to continue discussing NPRR1224 with the Stakeholders.

## Slide 7
Appendix

## Slide 8: Example Scenario
How to operate reliably on a day like this?
15:00
Operating Hour
Hourly Averaged Net Load Forecast & Generation Dispatch
Actual Net Load
Adjustment period
16:00
17:00
Move by dispatch
Highest 5-min Actual Net Load
Release of ECRS and
Deploy offline Non-Spin
Next RUC (i.e., Offline unit) 6 hours out
18:00
19:00
Offline Non-Spin 30 min out
Setting magnitude of ECRS to use 30 min out uncertainty ensures that ECRS is able to resolve any capacity needs until the offline Non-Spin unit comes on.

## Slide 9: Cold Start-up Time of OFFNS Resources in 2023
Cold Start time of units that were providing Non-Spin using OFFNS status was analyzed at 5-min resolution.
80th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
2 – Feb | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
3 – Mar | 18 min | 18 min | 18 min | 18 min | 24 min | 18 min
4 – Apr | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
5 – May | 18 min | 18 min | 18 min | 18 min | 24 min | 24 min
6 – Jun | 18 min | 18 min | 18 min | 30 min | 30 min | 30 min
7 – Jul | 18 min | 18 min | 24 min | 30 min | 30 min | 30 min
8 – Aug | 15 min | 18 min | 18 min | 30 min | 30 min | 18 min
Aug 17, 25, 30 | 18 min | 18 min | 30 min | 30 min | 30 min | 30 min
95th Percentile | a. HE1-2 & HE23-24 | b. HE3-6 | c. HE7-10 | d. HE11-14 | e. HE15-18 | f. HE19-22
1 – Jan | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
2 – Feb | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
3 – Mar | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
4 – Apr | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
5 – May | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
6 – Jun | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
7 – Jul | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
8 – Aug | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Aug 17, 25, 30 | 30 min | 30 min | 30min | 30 min | 30 min | 30 min
Notes: Decker Removed

## Slide 10: 2024 ECRS Quantities: Computed using 2024 and 2023 Methodology
The changes made to the 2024 ECRS methodology resulted in reducing ECRS quantities.
  On an average the ECRS quantity reduced by 442 MW in each hour (~21% reduction).
Avg | 2,194 | MW
Min | 1,203 | MW
Max | 3,548 | MW
Avg | 1,752 | MW
Min | 889 | MW
Max | 3,007 | MW