## Slide 1
San Antonio South Reliability II Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
April 15, 2024

## Slide 2: Overview
Brazos Electric Cooperative (BEC) initially submitted the San Miguel to Marion 345-kV Project for Regional Planning Group (RPG) review in September 2023
  This is a Tier 1 project that was estimated to cost $258.5 million
  To address the reliability need in the San Antonio area, located in Guadalupe, Wilson, and Atascosa Counties in the South and South-Central Weather Zones
  ERCOT identified separate reliability needs in the area and created the San Antonio South Reliability II Project

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review did not confirm the original project need as submitted by BEC
ERCOT’s independent review did confirm a need for a project under NERC and ERCOT Planning Criteria and redesignated the project as the San Antonio South Reliability II Project.
System improvement is needed to meet reliability planning criteria
Voltage Violations | Thermal Overloads | Unsolved Power Flow
0 | 13.4 miles of 138-kV line 45.8 miles of 345-kV line | 0

## Slide 5: Comparison of Project Options
ERCOT analyzed fifteen options and short-listed four options
Among the short-listed four options, Option 14 is the least cost solution, improves long-term load serving capability, improves operational flexibility and provides an additional transfer circuit from Southern Texas
Option 14 is the preferred option
 | Option 7 | Option 8 | Option 10 | Option 14
Meets ERCOT and NERC Reliability Criteria | Yes | Yes | Yes | Yes
Improves Long-Term Load Serving Capability | Yes | Yes | Yes (Better) | Yes (Better)
Improves Operational Flexibility | Yes | Yes | Yes | Yes (Marginally)
Additional transfer circuits from Southern Texas | 2 | 2 | 2 | 1
Requires CCN* (miles) | ~103.2 | ~89.4 | ~87 | ~58
Project Feasibility | Yes | Yes | Yes | Yes
Cost Estimate* ($M) | ~631 | ~570 | ~492 | ~435
* Cost estimates and CCN mileage were provided by TSPs

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 14 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 14 did not cause any new congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 14 to address the reliability need in the San Antonio area, located in Guadalupe, Wilson, and Atascosa Counties in the South and South-Central Weather Zones
TSP expects to implement the upgrades as follows:
  Construct the new Eastside 345/138-kV station by June 2028
  Rebuild JK Spruce to Pawnee 345-kV transmission line by December 2028
  Rebuild the Pawnee to Tango 345-kV transmission line by May 2029
Estimated Capital Cost: $435 Million
ERCOT will recommend that the ERCOT Board designate Option 14 as critical to the reliability of the ERCOT System pursuant to PUCT Substantive Rule 25.101(b)(3)(D)

## Slide 9: ERCOT Recommendation: Option 14
Rebuild the existing Spruce to Pawnee 345-kV single circuit into a 345-kV double circuit transmission line with a normal and emergency rating of at least 1,746 MVA per circuit, this transmission line will require approximately 45.8 miles of expanded Right of Way (ROW) which will be used to build one of the new circuits while the original circuit is left in service.
Rebuild the existing Pawnee to Tango 345-kV single circuit into a 345-kV double circuit transmission line with a normal and emergency rating of at least 1,746 MVA per circuit, this transmission line will require approximately 12.2 miles of expanded ROW which will be used to build one of the new circuits while the original circuit is left in service.
The Spruce to Pawnee 345-kV rebuild and the Pawnee to Tango 345-kV rebuild will be done without the need for extended outages.

## Slide 10: ERCOT Recommendation: Option 14 (continued)
Construct a new Eastside 345/138-kV station near Beck Rd. The Eastside 345/138-kV station includes two 345/138-kV autotransformers, each with normal and emergency ratings of at least 600 MVA, and will be interconnected as follows:
  Loop the existing Skyline to Spruce 345-kV double circuit transmission line into the new Eastside 345-kV station;
  Loop the existing Deely to Martinez 138-kV single circuit transmission line into the new Eastside 138-kV station;
  Loop the existing Deely to Walzem 138-kV single circuit transmission line into the new Eastside 138-kV station;
  Loop the existing Beck to Kirby 138-kV single circuit transmission line into the new Eastside 138-kV station; and
  Loop the existing Kirby to Sulphur 138-kV single circuit transmission line into the new Eastside 138-kV station.

## Slide 11: Option 14