## Slide 1
ERCOT Frequency Control Report
April 2024
ERCOT
Operations Planning
PDCWG | April 17, 2024

## Slide 2: Summary of March 2024
CPS1: 172.16%
Current CPS1 12-Month Rolling Average: 174.86%
0 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2022
2022 BAAL-003 FRM Performance: -1060.40
2024 RMS1 Statistics
  Mean: 15.07 mHz
  Min: 11.97 mHz
  Max 19.16 mHz
Energy Statistics
  Total Energy: 32,384,376 MWh
  Wind Energy: 10,215,704 MWh
  Percent Energy from Wind: 31.55%
  Solar Energy: 3,265,972 MWh
  Percent Energy from Solar: 10.09%
Minimum System Inertia
  Mean: 182,114 MW*s
  Max: 240,186 MW*s on March 5th
  Min: 129,920 MW*s on March 29th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Mar-24 CPS1 (%): 172.16
Notes: March CPS1 Score is 172.16%, there are no outliers below 100%.

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in March.

## Slide 6: 15-Minute Average CPS1%
Mar-24 CPS1 (%): 172.16
Notes: CPS1 score is above 150% for all but 15-minute intervals.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 174.86%
Notes: 12 month rolling average CPS1 score is 174.86 which is in line with expectations, and the CPS1 score for March is consistent with previous months.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is similar compared to 2023.
  2024 Stats:
  Mean: 15.07 mHz
  Min: 11.97 mHz
  Max 19.16 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
15.79 mHz on avg for March 2024

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between March 2023 and March 2024. Compared to last year, there are more instances of frequency hovering around the upper dead band.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile between March 2022 and March 2024. Similar to the previous slide, compared to 2022, there are more instances of frequency hovering around the dead bands.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2022 BAL-003 Selected Events – Update
Notes: BAL-003
These events will be selected and posted after April 1st, slide will be updated for upcoming PDCWG meetings.

## Slide 19: Op. Year 2022 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO = -471.0, FRM median = -913.56, FRM average = -992.
OP2022: FRO = -463.0, FRM median = -1060.40, FRM average = -1153.4

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 32,384,376 MWh

## Slide 22: Total Energy from Wind Generation
Notes:   10,215,704 MWH

## Slide 23: % Energy from Wind Generation
Notes: 31.55% of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 3,265,972 MWh ~ significant increase in solar from previous years.

## Slide 25: % Energy from Solar Generation
Notes: 10.09% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia in March 2024 = 129,920 MW*s on 3/29/2024
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
March Data:
Mean: 182,114 MW*s
Max: 240,186 MW*s on March 5th
Min: 129,920 MW*s on March 29th

## Slide 28: ERCOT Inertia 2013-2024
Date and Time | 2013 3/10 3:00 AM | 2014 3/30 3:00 AM | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 00:00 AM | 2022 03/21 01:00 AM | 2023 04/18 02:00 AM | 2024 03/29 03:00 AM
Min synch. Inertia (GW*s) | 132 | 135 | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 109 | 115 | 124 | 130
System load at minimum synch. Inertia (MW) | 24,726 | 24,540 | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 32,599 | 33,365 | 35,799 | 37,297
Non-synch. Gen. in % of System Load | 31 | 34 | 42 | 47 | 54 | 53 | 50 | 57 | 65 | 66 | 61 | 68
Notes: Summary of ERCOT intertia for the previous 10 years. Lowest inertia this year was on March 29th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 29: Questions?
Thank you!