## Slide 1
NPRR1234 and PGRR115
Overview, Key Concepts, and Impact to the Generation Interconnection Process
RIWG
June 12, 2024

## Slide 2: Introduction
ERCOT submitted NPRR1234 and PGRR115 on May 28, 2024.
These Revision Requests primarily address interconnection and modeling requirements for Large Loads (sites with aggregate peak Demand of 75 MW or more) and incorporate stakeholder feedback received on NPRR1191 and PGRR111 (withdrawn).
ERCOT plans to request that PRS refer NPRR1234 to ROS; PGRR115 will automatically be referred to ROS.

## Slide 3: NPRR1234
New Concepts and
Significant Changes from NPRR1191

## Slide 4: NPRR1234 – New Concepts & Significant Changes from NPRR1191
This NPRR implements the changed approach announced at the April 1 LFLTF. The following concepts from NPRR1191 do not appear in NPRR1234
  Registered Curtailable Loads (RCLs)
  Ramping limitations on Large Loads
  Voltage Ride Through (VRT) requirements for Large Loads
ERCOT remains concerned about the ramping and VRT issues and will explore other mitigation measures, such as procurement of additional AS and other system improvements.
Language in Section 16 requiring the registration of a load 25 MW or greater with ERCOT has been removed and replaced with a new requirement in Section 3.10.7.2 requiring identification and classification of loads 25 MW or greater in the Network Operations Model.

## Slide 5: Modeling of Loads 25 MW or Greater – Additional Details
TSPs will need to identify a load point or collection of load points serving a site with a historical, requested, or expected peak Demand 25 MW or greater in the ERCOT Network Operations Model.
RE will need to identify a load point or collection of load points serving a behind the meter load (excluding aux load) with a historical, requested, or expected peak Demand 25 MW or greater in the Resource Registration Data.
Load points serving sites 25-75 MW may include additional customers <25 MW.
For each load point identified, the TSP/RE must also provide the primary end-use activity from a list of broad categories.
The goal of these requirements is to allow ERCOT to improve its load forecasts and to provide real-time visibility to system operators.
For additional details https://www.ercot.com/files/docs/2024/06/02/PUBLIC_Overview_NPRR1234_PGRR115_June2024.pptx

## Slide 6: PGRR115
New Concepts and
Significant Changes from PGRR111

## Slide 7: PGRR115 – New Concepts & Significant Changes from PGRR111
The Large Load Interconnection Study (LLIS) process now applies to all Large Load interconnection requests, regardless of timeline.
All LLIS interactions will be between ERCOT and the interconnecting TSP (and IE/RE, if applicable).
  The Interconnecting Large Load Entity (ILLE) is still required to pay a LLIS fee to ERCOT. There is an option for the TSP to pay this fee on the customer’s behalf.
All interconnection requests subject to the LLIS must be studied in the Quarterly Stability Assessment (QSA) prior to energization.

## Slide 8: PGRR115 – LLIS Process Flow – High-Level Overview
TSP Requests LLIS
Kick-off Meeting Held
TSP Performs Studies
ERCOT Determines Reliability Limit(s)
Large Load Studied in QSA
Approved to Energize
TSP/RE Requests Approval to Energize
Large Load Added to Network Ops Model
Evidence of IA Provided to ERCOT

## Slide 9: PGRR115 – New Concepts & Significant Changes from PGRR111
Removed all requirements limiting when a Large Load can be added to SSWG cases. There are still requirements that must be met prior to adding a Large Load to the Network Operations Model.
All provisions allowing for a load intending to register as a Controllable Load Resource (CLR) to potentially interconnect additional MWs have been removed.
  This concept may be reintroduced in a future PGRR after approval of NPRR1188 and PGRR115.
Clearer requirements for what project modifications may require LLIS restudy are established in a new section 9.2.3

## Slide 10: PGRR115 – Additional Changes Impacting the GIM Process
An addition of a load 20 MW or greater at an existing Generation Resource will require a new reactive study that includes the load.
  This formalizes current practice under the interim Large Load process.
  The load will not require LLIS studies unless it is 75 MW or greater.
For a GIM request that also includes a Large Load, the PGRR allows for the FIS to be used to satisfy the LLIS provided the load is included and all required LLIS scenarios are studied.
  This would allow both generation and load to be evaluated in a single set of studies, eliminating duplicate work.
A new Section 5.2.10 has been added requiring the POI for all generation interconnections at transmission voltage to have a breaker.
  This formalizes current practice in the Planning Guide.