## Slide 1: Probabilistic Model for Determining Optimal AS Procurement
Andrew Reimers, Ph.D.
Deputy Director
Potomac Economics | ERCOT IMM
Technical Advisory Committee
June 24, 2024

## Slide 2: Model Summary
Objective: estimate the reliability value of different levels of reserves to inform procurement targets
Focusing on reserves responsive on the order of minutes to hours, i.e., ECRS, NSPIN, and DRRS
Model approach: determine how reserve levels (independent variable) influence LOLP given probabilistic distributions of unplanned outages and net load forecast error using 10k random draws of a Monte Carlo simulation for each hour in the study period
Historic hours from June 2023 to June 2024 are used as cases for comparing capacity at risk to different levels of reserves

## Slide 3: Outage Probability is a Function of Reserves vs. Capacity at Risk
Capacity at risk is a probabilistic function of unit trips and net load forecast error
  Unit trips are based on resource-level data for average operating time between trips
  Net load forecast error is a function of the forecast level for wind, solar, and load
  Outage risk and net load forecast error are functions of time-horizon, ie, 10-mins ahead vs 2-hours ahead
For each hour, Total Risk = Unit Trip MW + Net Load Forecast Error
For each of the 10k iterations of each hour, if Total Risk exceeds the level of reserves, that is counted as an outage
The probability of an outage is defined as #Outages/10k for each hour, and the annual LOLP can be derived from the probability of outages for each hour