## Slide 1
July 10, 2024
Balancing Operations Planning Staff
ESR Ancillary Service SOC Shortfall Analysis Report

## Slide 2: ESR AS MW Shortfall Introduction
NPRR1186 brought improvements to ERCOT systems to better account for state of charge (SOC). These changes now allow ERCOT’s EMS to preserve SOC in SCED dispatch to maintain needed SOC to support Ancillary Service (AS) obligation in the remainder of the hour.
The approved versions of NPRR1186 and NPRR1149 as approved do not consider SOC for accounting for shortfall. This led to TAC requesting a monthly report on tracking shortfall in AS obligation due to SOC.
ERCOT proposes this report template to provide insights into failure to provide and failure to perform due to low or insufficient SOC.
The charts on slide 3 and 4 have been built using SOC shortfall calculations over the hour which are converted to a MW shortfall value.
  Shortfall for each AS are assigned in this order (Non-Spin, ECRS, RRS, and Regulation).
  % Short of AS Responsibility is calculated as Hourly or Daily MW Short / Average Hourly Up AS Responsibility.
  AS Shortfall Cost ($) is calculated using the Market Clearing Price for Capacity (MCPC) of the Ancillary Services and the MW Short amount for each Ancillary Service for QSEs.
ERCOT intends to share a report with production data in Aug 2024 with the implementation of NPRR1186 in ERCOT systems.
  The data in this report uses preliminary data prior to official go-live of NPRR1186 to demonstrate the templates we are proposing for this report.

## Slide 3: Failure to maintain sufficient SOC necessary to provide their Ancillary Service Obligations if system conditions require (Month over Month)
An ESRs Shortfall is converted a to MW value and system-wide AS MW Short is computed at every interval (referred to as MW Short). Ancillary Service Shortfall costs are determined using MW Short and historical MCPC.
A Shortfall Hour occurs when an ESR’s integrated SOC shortfall exceeds the greater of 2MWhh or the lower of 8MWhh or 20% of the integrated SOC requirement over the course of an operating hour. (Proposed NPRR1186 compliance metric)
Observation:
[Insert Trend Observations]
Notes: SOC Shortfall (MWh) = SOC Requirement (MWh) – SOC (MWh)
MW Short (MW) = SOC Shortfall (MWh) / Time Remaining in Hour (h)
Integrated MW Short (MWh) = Integration of MW Short across all hours.
MW Short for a month (MW) = Integrated MW Short (MWh) / Hours where AS was carried in the month (h)
MW Short for a month is the value shown on these slides

## Slide 4: Failure to maintain sufficient SOC necessary to provide their Ancillary Service Obligations if system conditions require (April 2024)
Shortfalls are converted to MW values (referred to as MW Short) and grouped by HE and Day of the month. Ancillary Service Shortfall costs are determined using MW Short and historical MCPC.
Observation:
Top 3 day with largest AS MW short due to SOC: April 24, 20 and 21 largest AS MW short due to SOC
Top 3 day with largest AS $ short due to SOC: April 28, April 29, April 16
Top 5 Hours with AS MW short due to SOC: HE22, HE23, HE24, HE20, HE21

## Slide 5: Failure to perform during unit trips when carrying RRS with low SOC^.
  This data is sourced from the ERCOT BAL-TRE-001 FME tool considering. Low SOC is calculated using telemetered SOC, MXOS, MNOS as SOC % = ((SOC-MNOS)/MXOS)*100.
  * RRS-FFR performance is determined solely on sufficient MW response being provided.
  ^ Low SOC is set to 20% for this analysis, this is a configurable parameter.
 | RRS-PFR |  | RRS-FFR |  | RRS-FFR |  |  | 
Event Date | Evaluated ESRs | Failed ESRs | Evaluated Low SOC ESRs | Failed Low SOC ESRs | Evaluated ESRs | Failed ESRs* | Evaluated Low SOC ESRs | Failed Low SOC ESRs*
1/1/2024 20:13 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2/27/2024 9:21 | 50 | 14 | 1 | 1 | 8 | 0 | 0 | 0
2/28/2024 2:29 | 65 | 7 | 0 | 0 | 0 | 0 | 0 | 0
2/28/2024 10:15 | 61 | 8 | 0 | 0 | 0 | 0 | 0 | 0
3/12/2024 8:16 | 45 | 2 | 0 | 0 | 0 | 0 | 0 | 0
3/17/2024 15:16 | 67 | 33 | 1 | 0 | 0 | 0 | 0 | 0
3/24/2024 20:25 | 50 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4/8/2024 22:29 | 70 | 13 | 0 | 0 | 0 | 0 | 0 | 0
4/10/2024 20:55 | 57 | 2 | 0 | 0 | 0 | 0 | 0 | 0
4/13/2024 18:05 | 44 | 2 | 0 | 0 | 0 | 0 | 0 | 0
Observation: In April none of the ESRs carrying RRS that were evaluated during unit trips had a low SOC.
Notes: RRS-PFR is evaluated on ERCOT-RRS metric (1% droop). (BAL evaluation is in the appendix).

## Slide 6: Failure to meet GREDP/CLREDP when carrying AS with low SOC.
This table shows the GREDP and CLREDP performance in intervals where an ESR has an Ancillary Service Responsibility and is telemetering and SOC value less than 20% of their telemetered Maximum SOC.
  SOC % = ((SOC-MNOS)/MXOS)*100
  *Tables on this slide use a synthetic data set to illustrate capability.
Month | ESR GREDP Interval Failures | ESR CLREDP Interval Failures | Total Intervals on Low SOC with AS
April 2024 | 4 | 17 | 95
Observation:
In April, there are few instances of ESRs failing GREDP with low SOC and AS Responsibility.
Notes: ^ Low SOC is configurable.

## Slide 7: Summary
Now that NPRR1186 has been implemented, ERCOT plans to share a report using production data publicly starting in Aug. 2024 utilizing July 2024 data
ERCOT is seeking feedback on this report template and any additional analysis that may need to be included that could help share findings.
Please provide any feedback to Luis Hinojosa at jhinojosa@ercot.com by end of July.
Proposed Market Meeting Timeline for sharing template:
  July 23, 2024 WMWG
  July 31, TAC

## Slide 8: Appendix

## Slide 9: Failure to maintain sufficient SOC necessary to provide their Ancillary Service Obligations if system conditions require (April 2024 by QSE)
Observation: [Insert QSE Trend Observations]

## Slide 10: ESR failure to perform during unit trip frequency events with low SOC^
Event Date | BAL Evaluated Low SOC ESRs | BAL Low SOC Failed ESRs
1/1/2024 20:13 | 4 | 1
2/27/2024 9:21 | 11 | 1
2/28/2024 2:29 | 1 | 0
2/28/2024 10:15 | 3 | 1
3/12/2024 8:16 | 1 | 0
3/17/2024 15:16 | 5 | 1
3/24/2024 20:25 | 1 | 0
4/8/2024 22:29 | 5 | 1
4/10/2024 20:55 | 2 | 0
4/13/2024 18:05 | 2 | 1
  This data is sourced from the ERCOT BAL-TRE-001 FME tool and considers all ESRs evaluated by the tool. Low SOC is calculated using telemetered SOC, MXOS, MNOS as SOC % = ((SOC-MNOS)/MXOS)*100.
  ^ Low SOC is set to 20% for this analysis, this is a configurable parameter.
Observation: In April, there were two instances of ESRs failing the BAL-TRE-001 response metric.
Notes: This table shows the evaluation of BAL-TRE-001. (5% droop)