## Slide 1
Concept – Distribution Transformer Concept
Joel Koepke

## Slide 2: Goals
Provide Background
Discuss ERCOT Proposed Concept
Solicit Feedback

## Slide 3: Background

## Slide 4: Background: Transitioning to Simplified Modeling of DGR and DESRs
Transmission Network
Line
CIM Load
CIM Load
DGR Station
TSP Station
Transmission Network
TSP Station
Old-Style
New-Style
Multiple substations with load and generator modeled at distribution voltages
Single substation with load and generator modeled at transmission voltages

## Slide 5: ERCOT Proposal

## Slide 6: ERCOT Proposal – Addition of Distribution Transformer Class
ERCOT proposes the creation of an optional CIM class which contains key information on distribution transformers
Associated
Operations Model
A single load and multiple distribution generators can be associated to the new class

## Slide 7: ERCOT Proposal – Modification of Topology Processor
During topology processing, the Distribution Transformer will be converted to a transformer and a distribution-level bus will be created
The associated load and generation will be moved to the distribution bus
The distribution transformer is created…
…and connected to a new distribution bus…
…with the associated load and generator.
Topology Processor
Planning Model

## Slide 8: Current Approach: SODG
SODGs are not included in Operations topology but are added to new transmission-level buses in Planning cases via script.
Field
Model
Operations
Planning
SODGs are “mapped” to loads and are not topologically connected
Real-time applications do not meaningfully utilize SODG information
ERCOT adds SODGs to Planning cases at transmission-level via script

## Slide 9: Proposed Approach: SODG With Distribution Transformer
Field
Model
Operations
Planning
SODGs are “mapped” to loads and are not topologically connected
No change to real-time applications
Transformer and distribution bus created with load and SODG connected.
No Change
SODGs are not included in Operations topology but are added to new distribution-level buses in Planning cases via script.

## Slide 10: Current Approach: DGR/DESR
Field
Model
Operations
Planning
DGRs are topologically connected to the CIM load
Real-time applications do not incorporate DGR telemetry
Load and DGR on same planning bus at transmission-level voltage
DGRs are fully modeled in Operations and are on the same transmission-level bus as the associated load within Planning cases.
DGR=True
DGR=True
DGR=True

## Slide 11: Proposed Approach: DGR/DESR With Distribution Transformer
Field
Model
Operations
Planning
DGRs are topologically connected to the CIM load
Real-time applications do not incorporate DGR telemetry
Transformer and distribution bus created with load and DGR connected.
No Change
DGRs remain fully modeled in Operations but are added to new distribution-level buses in the Planning cases via script.

## Slide 12: Supplemental Slides

## Slide 13: Background: ERCOT State Estimator Enhancements
Capital project completed in early 2022 to modify the treatment of DGR/DESR in the State Estimator
Before Project
10MW
7MW
3MW
telemetry
telemetry
Calculated
DGR
Without code changes the DGR output would be double-counted
DGR output already captured in load telemetry
After Project
10MW
7MW
10MW
telemetry
telemetry
Calculated
Estimated flows are correct…
…because DGR telemetry is ignored by the SE