## Slide 1
Constraint Management Plan (CMP)
Alex Lee
Supervisor, Grid Analysis
WMWG
ERCOT Public
July 23, 2024

## Slide 2: Constraint Management Plan (CMP)
ERCOT Nodal Protocol Definition (Section 2)
A set of pre-defined manual transmission system actions, or automatic transmission system actions that do not constitute a Remedial Action Scheme (RAS), which are executed in response to system conditions to prevent or to resolve one or more thermal or non-thermal transmission security violations or to optimize the transmission system. CMPs may be developed in cases where studies indicate economic dispatch alone may be unable to resolve a transmission security violation or in response to Real-Time conditions where Security-Constrained Economic Dispatch (SCED) is unable to resolve a transmission security violation. ERCOT will employ CMPs to facilitate the market use of the ERCOT Transmission Grid, while maintaining system security and reliability in accordance with the Protocols, Operating Guides and North American Electric Reliability Corporation (NERC) Reliability Standards. CMPs are intended to supplement, not to replace, the use of SCED for prevention or resolution of one or more thermal or non-thermal transmission security violations.
Note: CMP is currently used for reliability purposes only, but NPRR1198/NOGRR258 will
allow CMP for economic purposes.

## Slide 3: Economic CMP Example
C6
G1
C5
C4
C3
C2
C1
G2
Normal Operation
300 MW
300 MW
Line Rating: 500
C6
G1
C5
C4
C3
C2
C1
G2
With CMP
300 MW
300 MW
Line Rating: 500
Bus 1
Bus 2
Bus 1
Bus 2
If the red transmission line has a fault, circuit breakers C4 and C5 will trip open to clear the fault. This results in excessive flow of 600 MW on the remaining green transmission line.
CMP may be to leave circuit breaker C6 open. If the red transmission line has a fault, circuit breakers C4 and C5 will trip open which will automatically trip G2 as well. The green transmission line will have 300 MW of flow which is under the rating.