## Slide 1
Analysis for NPRR1230:
Scenario-based Backcast for selected Operating Days in 2023
Gordon Drake
Dir. Market Design & Analysis

## Slide 2: Purpose
Present additional analysis as requested by TAC the potential impacts of NPRR 1230: Methodology for Setting Transmission Shadow Price Caps for an IROL in SCED using a backcast for selected Operating Days in 2023
Answer questions and discuss next steps to move this NPRR forward

## Slide 3: Recap: NPRR1230
Addresses operating conditions observed last summer for what are now the South Texas Export Interconnection Reliability Operating Limits (IROLs)
  ERCOT is currently using High Dispatch Limit (HDL) overrides to help mitigate the constraint
    Requires manual operator intervention and is not a market-based solution
    Difficult for the market to hedge/predict
NPRR1230 proposes to increase the Shadow Price Cap for some IROLs
  Establishes a transparent method for determining a new Shadow Price Cap for an individual IROL if needed
  Security-Constrained Economic Dispatch (SCED) can further manage the IROLs, allowing for the use of market-based tools
  Control Room Operators can focus on near-scarcity conditions

## Slide 4: Recap: IROL Shadow Price Cap Proposal
The Shadow Price Cap for each IROL will be set upon implementation to either:
  Shadow Price Cap for a Base Case/IROL constraint = $5,251/MWh
  Or =
New IROL Shadow Price Cap
Mitigated offer floor
Power balance penalty

## Slide 5: Analysis
Stakeholders requested additional analysis to understand the potential magnitude of pricing impacts with implementation of proposal under NPRR 1230
Next slides provide a backcast using 2023 to consider the potential impact under different scenarios
Things to keep in mind on backcast:
  Thermal cascading limits are calculated dynamically depending on grid conditions at that moment
  IROL did not exist in 2023; no straightforward way to recover the full dynamic nature of those limits
  Instead, the analysis used static limits based on the observed South Texas Export IROL limits in Real-Time from March – June 2024 when the constraints were binding
Summary information is included in these slides with further details in the appendix

## Slide 6: Backcast Input/Assumptions
Establish a baseline:
  Rerun SCED intervals where the South Texas – San Antonio post-contingency constraint was violated and include South Texas Export IROLs with a generic Max Shadow Price Cap of $5,251/MW.
Run NPRR1230 analysis:
  Shadow Price Cap set at $19,751/MW for the IROLs
  Ancillary Service release not adjusted
  HDL overrides relaxed
  Used 2023 historical loadings for line elements of South Texas IROLs
  Used 2024 historical line limits or South Texas IROLs to determine static limits
  Dynamic line ratings recently implemented for the lines comprising the IROLs not incorporated
  Two scenarios based on limit:
    Scenario 1 – Average historical limits of South Texas Export IROLs in RTM (March – June 2024) when binding
    Scenario 2 – 25th percentile of limits on South Texas Export IROLs in RTM (March – June 2024) when binding; illustrates impacts of operating to more conservative limits
    For each scenario, a corresponding baseline run is computed based on the current Max Shadow Price Cap of $5,251/MW and respective limits defined for the scenario
This approach is intended to isolate the specific impact of changing the Shadow Price Cap (i.e., NPRR1230), as opposed to capturing any impacts from simply having the new IROLs in place.
Note: The study is sequential run, where each SCED uses the output (base points, limits) from previous SCED rerun result as its input.
Limitation: The simulation models all Resources as perfectly following dispatch instructions. Additionally, behavioral factors cannot be simulated.

## Slide 7: Price/Value of Energy Recalculation Input/Assumptions
All prices/value of energy delta calculations set in relation to the baseline scenario mentioned in the previous slide.
Average prices/value of energy deltas only presented for binding intervals for the respective Operating Day (OD).
Load Zone (LZ) value of energy is defined as the product of:
  the 15-minute Load Zone Settlement Point Price in the Real-Time Market
  its associated Real-Time Adjusted Metered Load
* Note: Recalculated prices are presented w/o price adders.

## Slide 8: Number of Intervals per Operating Day where So. Texas – San Antonio Constraint at Max Shadow Price (violated)
Backcast focused on analyzing Operating Days in 2023 where the South Texas – San Antonio constraint was violated (at Maximum Shadow Price) during at least one SCED interval.
For Operating Days where the South Texas – San Antonio constraint was only binding, it is assumed that the IROLs would not be violated and hence the increased Maximum Shadow Price cap would not have a material impact on pricing outcomes.

## Slide 9: Constraint Violation Reduction (MWh) on South Texas – San Antonio Constraint and South Texas Export IROLs
Total violation volume across South Texas – San Antonio constraint and Two South Texas Export IROLs reduced in both scenarios
Scenario 2 (25th percentile limits) shows the least total violation volume
  The higher Maximum Shadow Price Cap and more conservative limit most effectively managed overloads on the South Texas – San Antonio Constraint

## Slide 10: Load Zone Value of Energy Total/Delta by Scenario
Scenario 2 (25th percentile limit) generated ~$1.2 billion greater difference in value of energy delta than Scenario 1 (average limit)

## Slide 11: Value of Energy Totals/Deltas by Load Zone and Scenario
The largest differences of the Load Zone value of energy are observed for Load Zone North and Load Zone Houston
Positive difference observed in Load Zone South
  Even with the suppressive impact of the increased congestion price on associated electrical buses, on specific Operating Days the increased scarcity in Load Zone South and positive System Lambda delta led to a net value of energy increase.

## Slide 12: Discussion
Previous slides provide illustrative impacts while noting some limitations given lack of historical IROLs
ERCOT is seeking direction/input from TAC leadership on NPRR 1230
  Further discussion or analysis?
  Proceed to vote?