## Slide 1
PDCWG Report to ROS
Chair: Kevin Bunch, EDF Trading North America
Vice Chair: Chad Mulholland, NRG
ROS
August 1st, 2024

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    2025 AS Methodology Review
    NOGRR 263 – Clarification of Controllable Load Resource Primary Frequency Response Responsibilities
    NOGRR 264 – Related to NPRR1235, Dispatchable Reliability Reserve Service as a Stand-Alone Ancillary Service
    NPRR 1235 – Dispatchable Reliability Service as a Stand-Alone Ancillary Service
    ERCOT Frequency Control Metrics and Regulation Reports
    TRE Report
    ICCP Tags for IRR Curtailments Discussion
    Analysis of Disturbances
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of June
  Frequency Control Report

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 395 MW/0.1 Hz
IMFR Performance currently
1431.00 MW/0.1HZ

## Slide 5
Questions?

## Slide 6: Frequency Control Report
February 2024

## Slide 7: CPS1 Performance

## Slide 8: RMS1 Performance of ERCOT Frequency
Notes: 14.28 mHz on avg for June 2024

## Slide 9: Frequency Profile Analysis

## Slide 10: Time Error Corrections
Notes: Time error toward the beginning of the month was due to abnormal loading conditions and weather patterns which contributed to forecasted errors. ERCOT increased the ACE integral feedback to adjust time error.

## Slide 11: ERCOT Total Energy
Notes: 44,675,848 MWh

## Slide 12: ERCOT Total Energy from Wind Generation
Notes:   10,029,421 MWH

## Slide 13: ERCOT % Energy from Wind Generation
Notes: 22.45% of total energy was provided by wind generation

## Slide 14: ERCOT Total Energy from Solar Generation
Notes: 4,979,491 MWh

## Slide 15: ERCOT % Energy from Solar Generation
Notes: 11.15% of total energy was provided by solar generation

## Slide 16: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in June 2024 = 228,743 MW*s on June 18th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
June Data:
Mean: 278,647 MW*s
Max: 320,334 MW*s on June 27th
Min: 228,743 MW*s on June 18th

## Slide 17: ERCOT Inertia Trend
Notes: Summary of ERCOT intertia for the previous 10 years. Lowest inertia this year was on March 29th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.