## Slide 1
Oncor Temple Area Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
July 31, 2024

## Slide 2: Overview
Oncor submitted the Oncor Temple Area Project for Regional Planning Group (RPG) review in January 2024
    This Tier 1 Oncor project submission was estimated to cost $120.7 million and will not require a Certificate of Convenience and Necessity (CCN)
    Addresses thermal violations in the Temple Area of Bell County
    ERCOT’s evaluation identified additional violations in the Killeen area and rest of Bell County, not addressed in the initial Oncor submission. ERCOT’s option is estimated to cost $272.6 million and will require a CCN

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in the Temple area, as seen in the Oncor submission and additional criteria violations in the Killeen area and rest of Bell County.
System improvement is needed to meet reliability planning criteria
Contingency Category | Thermal Overloads | Voltage Violations
N-0 (P0) | None | None
N-1 (P1, P2-1, P7) | None | None
G-1+N-1 (P3) | None | None
X-1+N-1 (P6-2) | Two 345/138-kV transformers, 18 miles of 138-kV line | 31

## Slide 5: Comparison of Project Options
ERCOT analyzed eleven options and short-listed three options
Among the short-listed three options, Option 5A improves long-term load serving capability, is the least cost solution and requires the least amount of CCN for the options that meet all of the ERCOT and NERC Reliability Criteria
Option 5A is the preferred option
* Cost estimates and CCN mileage were provided by TSPs
** The estimated cost does not include cost related to new CCN or land acquisition
 | Option 4A | Option 5A | Option 7A
Addresses the project needs | Yes | Yes | Yes
Meets ERCOT and NERC Reliability Criteria | No | Yes | Yes
Improves Long-term Load Serving Capability | Yes | Yes | Yes
CCN Required (~miles) | Yes (15.4) | Yes (15.4) | Yes (23.4)
Expected ISD (Month Year) | December 2028 | December 2028 | N/A
Construction Feasibility (Based on TSP assessment) | Yes | Yes | No
Capital Cost Estimates* (~$M) | 257.6 | 272.6 | 329.3**

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 5A and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 5A did not cause any new congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 5A to address reliability needs in the Bell County area
TSP expects to implement the upgrades by December 2028
Estimated Capital Cost: $272.6 million

## Slide 9: ERCOT Recommendation:
Install a second 345/138-kV autotransformer with nameplate rating of 600 MVA at Temple Pecan Creek Switch and loop the existing Bellfalls Switch – Temple Switch 345-kV transmission line into the Temple Pecan Creek 345-kV Switch by installing three new 345-kV circuit breakers in the existing 345-kV ring bus arrangement and three new 138-kV circuit breakers in the existing 138-kV breaker-and-a-half arrangement. Replace all existing 40 kA, 138-kV circuit breakers at Temple Pecan Creek Switch with 63 kA circuit breakers
Install a second 345/138-kV autotransformer with nameplate rating of 600 MVA at Temple Switch and rebuild the Temple 345/138-kV Switch with eleven 345-kV circuit breakers in a breaker-and-a-half arrangement and sixteen 138-kV circuit breakers in a breaker-and-a-half arrangement
Replace nine of the existing 40 kA, 138-kV circuit breakers at Temple Elm Creek Switch with 63 kA circuit breakers
Upgrade the existing Temple Pecan Creek Switch – Temple Elm Creek Switch 138-kV double-circuit transmission line with normal and emergency ratings of 493 MVA or greater, approximately 5.0-mile
Install a second circuit on the vacant position of the existing Temple Switch – Temple Pecan Creek Switch 138-kV double-circuit capable line with normal and emergency ratings of 486 MVA or greater, approximately 4.4-mile
Construct a new Boggy Creek 138/69-kV Switch approximately 3.58 miles south of the existing Temple 138-kV Substation. Install seven 138-kV breakers in breaker-and-a-half arrangement and two 69-kV breakers in single bus arrangement. Relocated the existing 138/69-kV autotransformer from Temple Switch to the new Boggy Creek Switch
Boggy Creek 138-kV Switch to be interconnected as follows:
  Install a new 69-kV transmission line on the vacant sides of the existing double-circuit capable structures of Taylor Switch – Temple Switch and Bob Poage – Seaton 69-kV transmission lines and connect the new 69-kV line to Minerva Switch at STR 3/5 to establish the Boggy Creek Switch – Minerva Switch 69-kV transmission line
  Establish the new Boggy Creek Switch – Temple Switch 138-kV transmission line by converting the 69-kV line between Boggy Creek Switch and Temple Switch to 138-kV operation
  Establish a normally open disconnect switch at Temple on the newly established Boggy Creek Switch – Temple Switch 138-kV transmission line with norming and emergency ratings of 197 MVA or greater, approximately 5.0-mile
  Disconnect the existing Temple Switch – Minerva Switch 69-kV at STR 3/5

## Slide 10: ERCOT Recommendation (Continued):
Construct an Oncor-owned New Bell County 138-kV Switch with four 138-kV breakers in a ring bus arrangement near the existing Bell County Switch and establish a tie to the existing Bell County Switch substation
Convert the existing Seaton – Bob Poage – Temple Taylor Valley – Bell County Switch 69-kV transmission lines to 138-kV operational with normal and emergency ratings of 214 MVA or greater, approximately 17.7-mile
Upgrade the existing Temple North – Pepper Creek Switch 138-kV double-circuit transmission line with a normal and emergency ratings of 486 MVA or greater, 2.2-mile per-circuit.
Install two new 600 MVA 345/138-kV Autotransformers at the existing Salado Switch and connect the 138-kV and 345-kV at Salado Switch.
Construct a New Bell County 138-kV Switch with four 138-kV breakers in a ring bus arrangement near the existing Bell County Switch and establish a tie to the existing Bell County Switch substation. New Bell County 138-kV Switch to be interconnected as follows:
  Keep the existing 345-kV double-circuit and the existing 345-kV line from Salado Switch – Knob Creek – Temple Switch but remove the existing 138-kV circuits from the existing 345-kV structures.
  Construct a New New Bell County Switch – Boggy Creek Switch – Temple Switch 138-kV transmission lines on new double-circuit structure with one circuit in place, utilizing the existing ROW with a normal and emergency ratings of 614 MVA or greater, approximately 7.7-mile.
  Construct a New Bell County Switch – Salado Switch 138-kV transmission line on new double-circuit structure with one circuit in place, utilizing the existing ROW, with normal and emergency ratings of 614 MVA or greater, approximately 7.8-mile
  Establish a Bell County Switch – New Bell County 138-kV connection
Upgrade the existing Temple Switch – Temple Southeast – Scott & White – Temple South – Belton 138-kV transmission lines with norming and emergency ratings of 486 MVA or greater, approximately 9.6-mile
Upgrade the existing Belton – Belton Southwest – Harker Heights South – Killeen Switch 138-kV transmission lines with normal and emergency ratings of 486 MVA or greater, approximately 17.2-mile
Upgrade the existing Belton – Nolanville – Harker Heights – Killeen Taft – Killeen Elms Rd – Killeen Switch 138-kV transmission lines with a norming and emergency ratings of 486 MVA or greater, approximately 19.8-mile.

## Slide 11: ERCOT Recommendation (Continued):
Upgrade the existing Temple Elm Creek Switch – Temple North 138-kV double-circuit transmission line with a normal and emergency ratings of 486 MVA or greater, approximately 0.6-mile per-circuit.
Construct the new Watercrest 138-kV Switch substation near Killeen Ft. Hood Switch in a 4-breaker ring bus arrangement and install one capacitor bank consisting of 110.4 Mvar in three 36.8 Mvar stages.
Close the normally open Killeen Ft. Hood – Killen Park Tap Street 138-kV transmission line.
Upgrade the existing Watercrest Switch – Killeen Taft 138-kV transmission lines with a normal and emergency ratings of 614 MVA or greater, approximately 7.9-mile.
Upgrade the existing Watercrest Switch – Killeen Switch 138-kV transmission lines with a normal and emergency ratings of 493 MVA or greater, approximately 7.5-mile.
Upgrade the existing Temple Switch – Seaton 138-kV transmission line with a normal and emergency ratings of 486 MVA or greater, approximately 2.7-mile.
Expand and convert the existing Bob Poage 69-kV substation to 138/69-kV Switch substation and install a new 100 MVA 138/69-kV Autotransformer.
Convert the existing Temple Taylor Valley 69-kV substation to 138-kV substation.

## Slide 12: ERCOT Recommendation: