## Slide 1: Reclosing Philosophy Near Inverter-Based Resources
Open Action Items | Responsible | Notes | Assigned
Develop guidance and recommendations for adjusting transmission reclosing and sectionalizing schemes that would significantly improve the IBR ride through probability and be reasonable to accomplish. Examples to look at would be no reclosing on 3 phase faults and adding current sensing directional intelligence on sectionalizing schemes to reduce number of times system is hit with faults. | IBRWG SPWG |  | 03/07/2023

## Slide 2: Reclosing Example
A
~
IBR
B
C
Station 2
D
E
Station 1
138 or 345 kV
Interconnection Line
Fault on IBR Tie Line:
CB A and CB C trip
Lead CB C Reclosing:
20 seconds open interval
Supervised reclose on a Dead Line only
Follow CB A Reclosing:
21 seconds open interval
Recloses one second following CB C on sync check
F
~
Generator

## Slide 3: Reclosing Example
A
~
IBR
B
C
Station 2
D
E
Station 1
138 or 345 kV
Interconnection Line
F
~
Generator
Fault on Adjacent Line
CB A, CB B, and CB D all trip to isolate the fault
Ring Bus Reclosing:
Lead CB A – 11 seconds open interval, then supervised reclose on sync check
Follow CB B – Recloses one second after CB A on sync check
Station 1 Reclosing:
10 cycles open interval, then supervised reclose for the following conditions: sync check, Dead Line

## Slide 4: Reclosing Example
Sync Check Settings
Voltage above 75% of nomial
Angle difference less than 40 degrees
Slip Frequency less than 0.067 Hz