## Slide 1
Resource Integration Topics
Jenifer Fernandes
ERCOT
Resource Integration Working Group
August 21, 2024

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.9
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.9, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic/PSCAD Model Review
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
PSCAD Model Quality Test, Unit Model Validation and Template is required. PSCAD template is required starting August 1st QSA.
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM and should include MQT

## Slide 4: Re-power – Current Requirements prior to re-power work
Part 2a approval is required prior to beginning any re-power work at the site.
  Approval is contingent on meeting the Re-power Compliance Checklist which includes:
    QSA
    PG 6.9
    SSR study if applicable
Concerns from RE that meeting all the requirements prior to decommissioning turbines/inverters could delay the project.

## Slide 5: Re-power – New requirements prior to re-power work
New requirements prior to beginning re-power work:
  FIS studies complete and current.
  QSE has submitted planned outages through the outage scheduler and the outage has been approved by ERCOT.
  Commissioning Plan submitted in RIOO-IS.
    The Commissioning Plan must have detailed decommissioning schedule of the old turbines and related equipment. The Commissioning Plan must also include the commissioning schedule of new turbines and related equipment.
  RE has affirmed in writing it understands the risks involved in decommissioning the turbines and related equipment without meeting the perquisites to be included in the QSA. RE also has affirmed it understands that new turbines could be impacted by a GTC or curtailed due to stability issue prior to Part 2b approval to synchronize.
  RE has affirmed in writing that any new equipment part of the re-power project will not be energized prior to receiving ERCOT approval of the Part 1.
  RE has affirmed in writing that the new or repowered turbines and related equipment will not be synchronized prior to receiving ERCOT approval of the Part 2b.

## Slide 6: PGRR114
Effective 8/1/2024
Planning Guide section 5.5(2):
  Before ERCOT approves Initial Energization for a project that will consume Load other than Wholesale Storage Load (WSL) and that is not behind a Non-Opt-In Entity (NOIE) tie meter:
    The Resource Entity must request an Electric Service Identifier(s) (ESI ID(s)) from the Distribution Service Provider(s) (DSP(s)) that will be serving the Load at the Resource site and provide the ESI ID(s) to ERCOT, as described in paragraph (2) of Protocol Section 10.3.2, ERCOT-Polled Settlement Meters; and
    (b) These ESI ID(s) must be established in the ERCOT Settlement system in a state that allows for the Load to be properly settled to the appropriate Qualified Scheduling Entity (QSE).

## Slide 7: PGRR112
Effective 12/1/2024, affects Feb 1st 2025 QSA
PG 5.3.2.5 (7):
  The final FIS element(s) report shall be deemed complete and marked “final” via the online RIOO system at least 45 days prior to the quarterly stability assessment deadline defined in paragraph (2) of Section 5.3.5, ERCOT Quarterly Stability Assessment.
PG 5.3.2.5 (9):
  During the time after the FIS is completed and before Initial Synchronization, the IE shall notify both ERCOT and the lead TSP(s) of any changes to the assumptions used for the FIS along with a detailed written explanation of why the changes were made. If the changes substantially differ from the assumptions used for the FIS, ERCOT and the TSP(s) shall determine the impact of the changes on the results of the FIS and, if applicable, SSR studies.

## Slide 8: PGRR112
PG 5.3.5 (4)(b):
The IE has provided all generator data in accordance with the Resource Registration Glossary, Planning Model column, including but not limited to steady state, system protection and stability models.
(i) The IE shall submit the final dynamic data model at least 45 days prior to the quarterly stability assessment deadline described in paragraph (2) above. If ERCOT is unable to complete its review prior to the quarterly stability assessment deadline, ERCOT shall not include the Generation Resource or Settlement Only Generator (SOG) in that quarterly stability assessment.
(ii) Changes to the dynamic data model after the stability study is deemed complete may subject the Generation Resource or SOG to modification of one or more FIS study elements as defined in paragraph (9) of Section 5.3.2.5, FIS Report and Follow-up. If ERCOT and the lead TSP(s) determine that modifications to one or more FIS study elements are required, then ERCOT shall not include the Generation Resource or SOG in a quarterly stability assessment until the revised FIS has been completed in accordance with paragraph (4)(c)(i) below.
(iii) If an IE submitted a final dynamic data model at least 45 days prior to the quarterly stability assessment deadline but ERCOT determines that the Generation Resource or SOG is ineligible to be included in a quarterly stability assessment pursuant to paragraphs (4)(b)(i) or (4)(b)(ii) above, ERCOT will send a notification to the IE.

## Slide 9: Commissioning Requests Submission- New Email Address
ERCOT has established a new, dedicated email address for Market Participants to submit new generator Commissioning Checklist for review.
Starting June 10, 2024, all new Commissioning Checklists (Parts 1-3) should be emailed to CommissioningRequests@ercot.com in addition to being submitted to RIOO-IS.
Commissioning Checklists (Parts 1-3) submitted to ResourceIntegrationDepartment@ercot.com after June 21, 2024, will not be processed.
Commissioning Plans should not be emailed for review to the new Commissioning Request email address.

## Slide 10: Generation Interconnection Requests
1,858 active generation interconnection requests totaling 365 GW as of July 31st, 2024 (Solar 154 GW, Wind 34 GW, Gas 22 GW, and Battery 152GW) (Excludes capacity associated with projects designated as Inactive per Planning Guide Section 5.7.6)
Chart: Monthly Capacity by Fuel Type plus Project Count, 13-Month Rolling Basis
| Jul-23 | Aug-23 | Sep-23 | Oct-23 | Nov-23 | Dec-23 | Jan-24 | Feb-24 | Mar-24 | Apr-24 | May-24 | Jun-24 | Jul-24
Natural Gas | 12.3684 | 11.8415 | 11.3837 | 13.6376 | 15.4573 | 15.4828 | 15.5461 | 16.0221 | 15.4289 | 15.5729 | 15.9379 | 17.0887 | 22.1599
Nuclear | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Coal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind | 28.615 | 32.0345 | 31.6397 | 31.9157 | 32.5096 | 34.5909 | 36.2609 | 37.215 | 35.1196 | 32.9563 | 33.8868 | 31.4522 | 33.7315
Solar | 133.9786 | 136.1652 | 141.3153 | 143.2215 | 142.606 | 145.654 | 148.1353 | 152.0979 | 155.2725 | 152.9165 | 154.2253 | 152.4334 | 154.4072
Biomass | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0.053 | 0 | 0 | 0 | 0 | 0 | 0
Battery | 110.408 | 111.579 | 114.5631 | 120.5341 | 124.9412 | 127.0677 | 133.5925 | 140.2192 | 141.4837 | 145.0004 | 149.0016 | 147.7434 | 151.811
Other | 2.3856 | 2.235 | 2.235 | 2.235 | 2.385 | 2.367 | 2.2468 | 2.9668 | 2.3319 | 2.3319 | 2.3319 | 2.3319 | 2.5619
Total Project Count | 1500 | 1537 | 1580 | 1628 | 1656 | 1671 | 1731 | 1783 | 1775 | 1780 | 1813 | 1812 | 1858
Cancelled Project Count | 16 | 7 | 15 | 16 | 10 | 12 | 12 | 13 | 64 | 15 | 9 | 27 | 5

## Slide 11: Generation Interconnection Requests
Small Gen- 31 projects Not Model Ready, 46 projects Model Ready
Chart: Small Generator Monthly Capacity by GIM Milestone plus Project Count, 13-Month Rolling Basis
| Jul-23 | Aug-23 | Sep-23 | Oct-23 | Nov-23 | Dec-23 | Jan-24 | Feb-24 | Mar-24 | Apr-24 | May-24 | Jun-24 | Jul-24
# Not Model Ready | 25 | 31 | 40 | 41 | 44 | 41 | 42 | 43 | 39 | 42 | 39 | 34 | 31
# Model Ready | 28 | 30 | 32 | 32 | 30 | 28 | 29 | 27 | 29 | 33 | 41 | 44 | 46
MW Capacity | 501.55 | 573.37 | 682.72 | 692.56 | 701.31 | 651.14 | 670.99 | 660.94 | 641.11 | 705.33 | 745.73 | 725.74 | 715.94

## Slide 12: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 13: Questions?
Thank you!