## Slide 1
ERCOT 2024 UFLS Survey Results
Jake Pedigo
ERCOT Compliance

## Slide 2: Background on the ERCOT UFLS Survey and Requirements
ERCOT coordinated and conducted the 2024 survey with ERCOT Transmission Operators (TOs.) The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event.
The table below is taken from the ERCOT Nodal Operating Guides, Section 2.6.1 (1), Requirements for Under-Frequency Load Shedding, and lists the required load shed amounts:
Frequency Threshold | Load Relief
59.3 Hz | At least 5% of the TO Load
59.1 Hz | A total of at least 5% of the TO Load
58.9 Hz | A total of at least 15% of the TO Load
58.7 Hz | A total of at least 15% of the TO Load
58.5 Hz | A total of at least 25% of the TO Load
ERCOT Nodal Operating Guides, Section 2.6.1 (2)
  ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.

## Slide 3: 2024 UFLS Survey Activity Timeline
Below is the timeline reflecting the survey dates and activities:
Date | Activity
March 13th | Announcement of survey timeline to OWG
March 28th | Market Notice sent to Authorized TO Representatives
May 9th @ 11:00 AM | Date and time of survey
July 12th | Survey results due to ERCOT
August 15th | Results reported to OWG
September 9th | Results reported to ROS
September 19th | Results reported to TAC

## Slide 4: Survey Results
The overall results of the 2024 UFLS survey are reflected in the table below:
TOs successfully met the UFLS requirements for all five thresholds.
The ERCOT load at the time of the survey was 55,616 MW. In comparison, the 2023 survey overall result was 30.95% at 52,679 MW of load.
Frequency Threshold | Minimum Requirement | Survey Measurement
59.3 Hz | At least 5% of the TO Load | 6.97%
59.1 Hz | A total of at least 5% of the TO Load | 7.43%
58.9 Hz | A total of at least 15% of the TO Load | 18.79%
58.7 Hz | A total of at least 15% of the TO Load | 19.15%
58.5 Hz | A total of at least 25% of the TO Load | 30.83%

## Slide 5: Survey Results – NOGRR247
NOGRR247 modifies the ERCOT automatic UFLS program by increasing the number of Load shed stages from three to five and changing the TO Load relief amounts to uniformly increment by 5% for each stage. The NOGRR also adds a UFLS minimum time delay of six cycles (0.1 seconds). Additionally, this NOGRR revises the grey-box language from NOGRR226 in Section 2.6.1 to provide that the TO Load value used to determine the TO Load at each frequency threshold in Table 1 will be the value of TO Load at the time frequency reaches 59.5 Hz, rather than the value of TO Load at the time of reaching each successive frequency threshold, consistent with the current method for determining TO Load in Table 1. Implementation is voluntary at this time, but will be mandatory on or before October 1, 2026:
Frequency Threshold | Minimum Requirement | Delay to Trip
59.3 Hz | At least 5% of the TO Load | At least six cycles but no more than 30 cycles
59.1 Hz | A total of at least 10% of the TO Load | At least six cycles but no more than 30 cycles
58.9 Hz | A total of at least 15% of the TO Load | At least six cycles but no more than 30 cycles
58.7 Hz | A total of at least 20% of the TO Load | At least six cycles but no more than 30 cycles
58.5 Hz | A total of at least 25% of the TO Load | At least six cycles but no more than 30 cycles
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements

## Slide 6: Survey Results – NOGRR247 (cont.)
ERCOT TOs have begun implementation of the additional UFLS stages. Two TO Entities have submitted capability totaling:
Frequency Threshold | Minimum Requirement | Survey Percentage | Survey Load
59.1 Hz | A total of at least 10% of the TO Load | .46% | 256.09 MW
58.7 Hz | A total of at least 20% of the TO Load | .35% | 197.04 MW

## Slide 7: Optional Supplemental/Anti-Stall UFLS Stages
ERCOT Nodal Operating Guides 2.6.1 (3)
A TO may meet the Load relief requirements of the Supplemental anti-stall UFLS stages by utilizing Load that would otherwise be utilized to meet the 59.1 Hz, 58.9 Hz, 58.7 Hz, and 58.5 Hz standard UFLS stages. In this circumstance, the TO’s Load relief responsibility at the 59.1 Hz, 58.9 Hz, 58.7 Hz, and 58.5 Hz standard UFLS stages is reduced by the amount of Load already shed in the supplemental anti-stall UFLS stages. A TO may not meet the Load relief requirements of the supplemental anti-stall UFLS stages by utilizing Load that the TO needs to meet the 59.3 Hz standard UFLS stages. Implementation is voluntary at this time, but will be mandatory no earlier than October 1, 2026:
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements
Frequency Threshold | Minimum Requirement | Delay to Trip
59.5 Hz | At least 1.5% of the TO Load | 90 seconds
59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds
59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds

## Slide 8: Survey Results – NOGRR226
ERCOT TOs have begun implementation of the Supplemental/Anti-Stall UFLS Stages. Two TO Entities have submitted capability totaling:
Frequency Threshold | Minimum Requirement | Survey Percentage | Survey Load
59.5 Hz | At least 1.5% of the TO Load (90 Sec) | .04% | 24.85 MW
59.5 Hz | A total of at least 3% of the TO Load (120 Sec) | .13% | 49.11 MW
59.5 Hz | A total of at least 4.5% of the TO Load (150 Sec) | .20% | 37.07 MW

## Slide 9: Conclusion
ERCOT Compliance appreciates all entities participation in the 2024 UFLS Survey.
Questions or Comments?