## Slide 1
PRS Meeting
September 12, 2024
NPRR1226 Demand Response Monitor- ERCOT Review

## Slide 2: NPRR1226 ERCOT Review
The data requested is intended to only provide an indicator of the direction certain ”ERCOT identified” transmission loads are responding. Only certain non-conforming transmission connected loads will be aggregated in the data set.
This is not intended to be an accurate real-time estimation of aggregate Demand Response occurring in ERCOT.

## Slide 3: NPRR1226 ERCOT Review
Data Requirements
  Need to identify which State Estimator Loads (SEL) include meaningful MWs of non-conforming load (load that is not impacted by weather conditions).
    SELs selected by ERCOT
    SELs selected have historically responded to LMPs, 4CP/Near 4CP, voluntary energy conservation notices, or other ERCOT actions.
  Once identified aggregate these SELs into a single real-time value for each SCED run over the last two hours.
  Determine peak consumption of the aggregate SELs
    Language currently in NPRR will result in erroneous response values
    Suggest using a meter-before approach (see next slide)
  Calculate running Demand Response by comparing the single real-time values to the peak consumption.

## Slide 4: NPRR1226 ERCOT Review
Issues Identified with NPRR
  A 2 hour look back for determining peal interval as suggested in the NPRR can result in a false recovery from load reduction events. Historically some load reduction events have been shown to last longer than 2 hours (E.g., 4CP events can start as early as interval 60 and conclude at interval 80 or later).
  This could be resolved by using a “meter-before” approach that identifies a point in time just prior to when a predetermined change in the load point occurred.
  Suggest adopting protocol language that is less prescriptive to address this issue.

## Slide 5: NPRR1226 ERCOT Review
ERCOT currently provides similar data to the ERCOT Control room on the Steel Mill Loads and LFLs. The graphic does not provide a separate response value.
  Steel Mills and LFLs are shown separately (not recommended for public)
  Graphs telemetered aggregate load to LMP
NPRR provides ERCOT sole responsibility of identifying which SELs to include in the aggregation. Any public reporting of which SELs are included must be avoided.
Issue of the “quality of the data” raised at previous PRS meeting. This may not be an issue once it’s understood the information provided is intended to solely be a DR indicator and not a real-time ERCOT wide estimate of DR.
Transmission switching can be an issue.