## Slide 1: LCRA DPC process
Blake Holt | Kenton Kwan
TWG – 10.24.2024

## Slide 2: DPC NOMCR submissions
    Submission scenarios:
      When an operational line (static and dynamic) or transformer (static) ratings get published by our engineering team and they are different from the ratings in the ERCOT Model.
      When an operational line or transformer impedances get published by our engineering team and they are different from the impedances in the ERCOT model.
      We run tools that compare line ratings every month. If we find some discrepancies in the published ratings and ERCOT Model, we submit a DPC to update the model immediately.
      On the day of energization, only if the ratings and impedances do not match up (very rare situation)

## Slide 3: DPC NOMCR goals
      Timing - Since we work on capital projects, we try to submit:
        Standard NOMCRs (4 months ahead of time) for all the new equipment additions.
        Interim NOMCRs (3 weeks ahead of time) when the for-construction ratings and impedances are published.
      Procedures – set according to rules and guidelines for submission
        We submit DPC NOMCR with only 1 type of change. If we have ratings and impedance changes, we submit 2 DPC NOMCR.
        We send out an email as soon as we get the NOMCR submitted to notify the ERCOT network modeling group
        We attach a DPC request form and reasoning document with the NOMCR
        Once the DPC NOMCR is processed, we update the EMS model immediately to reflect the change for our operations to observe.

## Slide 4: DPC CAMR submissions
    Submission scenarios:
      When equipment is closed or opened that would cause a different set of equipment to operate for a fault. This mainly happens when normally open equipment is closed that would bypass the breakers that would usually operate for a line or transformer fault.
          We submit a DPC CAMR to enable manual contingencies within 3 business days of the effective date. If a contingency is needed to be created to reflect this new configuration, then we will attach an excel sheet with the proposed definitions(s) in the same CAMR.
          We will submit a separate DPC CAMR within 3 business days of the configuration returning to normal.
      When new equipment is being energized while the old equipment it is replacing is still in the model. Since pseudo switches are used, manual contingencies are often needed to correctly define the contingencies since the PGCs (Programmatically Generated Contingencies) are not correct in this case until the old equipment is removed.
          The definitions for the manual contingencies in this situation will often be submitted in the regular CAMR window as disabled to coincide with the same production load date as the NOMCR that adds the new equipment to the model.
          Enabling the manuals for when the new equipment actually energizes follows the regular DPC CAMR timeline of 3 days.
      When active contingencies are noticed to be incorrect and either need to be disabled, enabled, or edited.