## Slide 1
AEPSC Brownsville Area Improvements Transmission Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
October 30, 2024

## Slide 2: Overview
American Electric Power Service Corporation (AEPSC) submitted the Brownsville Area Improvements Transmission Project for Regional Planning Group (RPG) review in March 2024
    This Tier 1 AEPSC proposed project submission was estimated to cost $387.7 million and will require a Certificate of Convenience and Necessity (CCN)
    Addresses thermal overloads and voltage violations in the Brownsville Area in Cameron County

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in the Brownsville Area in Cameron County
System improvement is needed to meet reliability planning criteria
Contingency Category | Thermal Overloads | Voltage Violations
P0: N-0 | None | None
P1, P2-1, P7: N-1 | 92.6 miles of 138-kV lines | 1
P3: G-1+N-1 | 8.4 miles of 138-kV line | None
P6-2: X-1+N-1 | One 345/138-kV transformers, 4.9 miles of 138-kV line | None

## Slide 5: Comparison of Project Options
ERCOT analyzed ten options and short-listed four options
Among the short-listed four options, Option 2A addresses the reliability violations, and is the least expensive option. Option 2A also provides additional operational flexibility and improves long-term load-serving capability.
Option 2A is the preferred option
* Cost estimates and CCN mileage were provided by TSPs
 | Option 2A | Option 5A | Option 7 | Option 8
Meets ERCOT and NERC Reliability Criteria | Yes | Yes | Yes | Yes
Improves Long-Term Load-Serving Capability | Yes | Yes | Yes | Yes
Improves Operational Flexibility | Yes | Yes | Yes | Yes
Requires CCN (~miles)* | Yes (26.0) | Yes (43.4) | Yes (33.3) | Yes (18.8)
Project Feasibility | Yes | Yes | Yes | Yes
Cost Estimate (~$M)* | 423.8 | 458.3 | 427.0 | 501.6

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 2A and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 2A did cause a new congestion within the study area
    Upgrade of new congested line did not yield any economic benefit and therefore will not be recommended for upgrade as part of this project
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Option 2A to address reliability needs in the Brownsville Area in Cameron County
TSPs expect to implement the upgrades by May 2029
Estimated Capital Cost: $423.8 million

## Slide 9: ERCOT Recommendation:
Expand the planned Chalybe 138-kV substation to install a new 345-kV ring-bus arrangement, with two 345/138-kV autotransformers with normal and emergency ratings of at least 675 MVA;
Construct a new Chalybe to Kingfisher 345-kV double-circuit transmission line with normal and emergency ratings of at least 2668 MVA per circuit, on a new ROW, approximately 22.0-mile;
Construct a new Chalybe to Palmito 345-kV double-circuit transmission line with normal and emergency ratings of at least 2668 MVA per circuit, on a new ROW, approximately 2.0-mile;
Construct a new Chalybe to Stillman 138-kV single-circuit transmission line with normal and emergency ratings of at least 987 MVA, on a new ROW, approximately 2.0-mile;
Rebuild the existing La Palma to Fresno 138-kV single-circuit transmission line with normal and emergency ratings of at least 535 MVA, approximately 10.3-mile;
Rebuild the existing Fresno to Stillman 138-kV single-circuit transmission line with normal and emergency ratings of at least 717 MVA, approximately 12.0-mile;
Rebuild the existing Military to Villa Cavazos 138-kV single-circuit transmission line with normal and emergency ratings of at least 717 MVA, approximately 10.0-mile;
Rebuild the existing La Palma to Villa Cavazos 138-kV single-circuit transmission line with normal and emergency ratings of at least 535 MVA, approximately 12.2-mile; and
Expand the planned Chalybe 138-kV substation to install two +/-150 MVAr STATCOMs.

## Slide 10: ERCOT Recommendation: