## NPRR 1219 CHANGES
Changes Impacting the December CDR Report Based on NPRR1219
Peak Net Load Information: Planning Reserve Margin (PRMs) and associated loads and resource information will be added for the forecasted peak Net Load hour by year and season.
Shift to Effective Load Carrying Capabilities (ELCCs): Instead of using peak average capacity contributions for wind and solar resources, the CDR will now utilize ELCCs to represent their availabilities. ELCCs will also be estimated for battery energy storage systems.
Expanded Reporting Timeframe: The report will now include PRMs, associated loads, and resources for all four seasons (summer, winter, spring, and fall). Previously, only summer and winter seasons were included. The December 2024 CDR will cover the Summer and Winter seasons, whereas full seasonal reporting will be implemented for the May 2025 CDR.
Introduction of New Solar Regions: Three new solar regions (West, Far West, and Other) are introduced to enable more accurate solar capacity availability forecasts. Previously, a single system capacity availability forecast was used.
Updated Criteria for Planned Resources: The criteria for including planned resources in the CDR has been expanded to include ERCOT notification that a project developer has provided the required financial security for interconnection facility construction. See ERCOT Planning Guide Section 6.9(1)(d)(ii)(B).
Inclusion of Publicly Announced Planned Retirements: A new category for planned retirements has been added to account for Generation Resources that have a publicly announced retirement plan but haven't yet submitted a formal Notification of Suspension of Operations (NSO) to ERCOT.
Inclusion of Distribution Voltage Reduction (DVR): Distribution voltage reduction will now be included as a load-reducing adjustment for Firm Peak Load calculation.
Inclusion of Energy Storage Resources (ESRs): Existing and planned ESRs will be factored into the PRM calculations as available capacity. Battery ESRs will be categorized based on their maximum (or design) duration capabilities.
Revised Emergency Response Service (ERS) Methodology: The methodology for estimating forecasted ERS capacity has been modified to match the most recent ERS procurement amounts and allow ERCOT to make adjustments based on anticipated ERS program changes. This approach avoids unrealistic forecasted year-to-year volatility caused by averaging three-year historical ERS amounts.
Elevated Probability-of-Return Threshold for Mothballed Generation Resources: The threshold for including mothballed Generation Resources in the PRM calculations has been raised from 50% to 75%.

## TitlePage
For discussion purposes only
Report on the Capacity, Demand and Reserves
(CDR) in the ERCOT Region, 2025-2029
Preliminary Mock-up for December 2024 CDR

## Contents
Table of Contents
Tab | Notes
Disclaimer | Please read
Executive Summary | Synopsis and highlights of the CDR report
DATA TABLES
Spring Summary | [To be included in the May 2025 CDR] Shows load forecasts, resource capacities and reserve margins for the next five spring seasons, for both the expected Peak Load hour and Peak Net Load Hour
Summer Summary | Shows load forecasts, resource capacities and reserve margins for the next five summer seasons, for both the expected Peak Load hour and Peak Net Load Hour
Fall Summary | [To be included in the May 2025 CDR] Shows load forecasts, resource capacities and reserve margins for the next five fall seasons, for both the expected Peak Load hour and Peak Net Load Hour
Winter Summary | Shows load forecasts, resource capacities and reserve margins for the next five winter seasons, for both the expected Peak Load hour and Peak Net Load Hour
Unit Details | List of registered resources and capabilities used in determining the capacity contributions by Season
New CDR-Eligible Resources | A table listing those planned resources that have meet the criteria to be included in the CDR since the last CDR release
Capacity by Resource Type | A table that lists installed capacities by fuel/technology type categories
Load-Resource Scenarios | Presents condensed demand-resource summaries for the summer and winter seasons based on alternative peak demand and/or resource scenarios
ELCCs | A table that lists Effective Load Carrying Capabilities (ELCCs) for Inverter Based Resources
DOCUMENTATION
Acronyms | List of acroynms used in the CDR data tables
Definitions | Definitions of terms used in the CDR
Wind-Solar Region Mapping | Tables that list the counties in the ERCOT region assigned to the CDR Wind and Solar Regions
Background | An overview of the CDR's purpose and key concepts needed to interpret results

## Disclaimer
Disclaimer
FOR PLANNING PURPOSES ONLY
This CDR report has been prepared using data provided by ERCOT and Market Participants. The data may contain errors or become obsolete and thereby affect the accuracy of report results. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT REPORT IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of the CDR report and its accuracy should be confirmed by each ERCOT Market Participant that contributed data.

## Executive Summary
CDR Report - Executive Summary
Load and Resource Highlights
Peak Load Forecast
| ● | Text
| ● | Text
Planning Reserve Margins
| ● | Text
| ● | Text
Sample Charts - Not Real Data
Forecasted Resource Trends
| ● | Text
| ● | Text
Significant Resource Status Changes
| ● | Text
| ● | Text
Events and Emerging Risks Impacting Resource Adequacy |  |  | Section still under consideration
| ● | Text
| ● | Text

## Spring Summary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Spring Summary: 2025-2029
|  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029
|  | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [1] less [2] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [4] less [5] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [7] less [8] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [10] less [11] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [13] less [14]
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15]
Load Forecast and Adjustments, MW:
Base Summer Peak Load (assuming normal weather)
less: Load Resources providing Responsive Reserves
less: Load Resources providing Non-Spinning Reserves
less: Load Resources providing ERCOT Contingency Reserve Service (ECRS)
less: Controllable Load Resources not included in other adjustments
less: Emergency Response Service (10- and 30-min ramp products)
less: TDSP Standard Offer Load Management Programs
less: Distribution Voltage Reduction
Firm Peak Load, MW
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | [1]: 3208; [4]: 3497; [7]: 3786; [10]: 4076; [13]: 4367
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
Installed Summer-rated Capacity, Thermal
Hydroelectric, Peak Average Capacity Contribution (80% of installed capacity)
Switchable Capacity
less: Switchable Capacity Unavailable to ERCOT
Available Mothballed Capacity (Units with reported return probabilities ≥ 75%)
Capacity from Private Use Networks
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
RMR Capacity to be under Contract
Capacity Pending Retirement
Operational Generation Capacity, Total
Non-Synchronous Ties (Based on average net import contribution during the summer 2023 EEA event)
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
Thermal Resources
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
Unconfirmed Planned Retirements
Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements
Total Capacity
Reserve Margin | bar: [1] to [9]
(Total Resources - Firm Load Forecast) / Firm Load Forecast
| Firm Peak Load plus New Contracted Loads Reported by TSPs | [1]: 2025; [3]: 2026; [5]: 2027; [7]: 2028; [9]: 2029
|  | #REF! |  | #REF! |  | #REF! |  | #REF! |  | #REF!

## Summer Summary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Summer Summary: 2025-2029
|  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029
|  | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [1] less [2] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [4] less [5] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [7] less [8] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [10] less [11] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [13] less [14]
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15]
Load Forecast and Adjustments, MW:
Base Summer Peak Load (assuming normal weather)
less: Load Resources providing Responsive Reserves
less: Load Resources providing Non-Spinning Reserves
less: Load Resources providing ERCOT Contingency Reserve Service (ECRS)
less: Controllable Load Resources not included in other adjustments
less: Emergency Response Service (10- and 30-min ramp products)
less: TDSP Standard Offer Load Management Programs
less: Distribution Voltage Reduction
Firm Peak Load, MW
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | [1]: 3208; [4]: 3497; [7]: 3786; [10]: 4076; [13]: 4367
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
Installed Summer-rated Capacity, Thermal
Hydroelectric, Peak Average Capacity Contribution (80% of installed capacity)
Switchable Capacity
less: Switchable Capacity Unavailable to ERCOT
Available Mothballed Capacity (Units with reported return probabilities ≥ 75%)
Capacity from Private Use Networks
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
RMR Capacity to be under Contract
Capacity Pending Retirement
Operational Generation Capacity, Total
Non-Synchronous Ties (Based on average net import contribution during the summer 2023 EEA event)
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
Thermal Resources
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
Unconfirmed Planned Retirements
Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements
Total Capacity
Reserve Margin | bar: [1] to [9]
(Total Resources - Firm Load Forecast) / Firm Load Forecast
| Firm Peak Load plus New Contracted Loads Reported by TSPs | [1]: 2025; [3]: 2026; [5]: 2027; [7]: 2028; [9]: 2029
|  | #REF! |  | #REF! |  | #REF! |  | #REF! |  | #REF!

## Fall Summary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Fall Summary: 2025-2029
|  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029
|  | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [1] less [2] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [4] less [5] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [7] less [8] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [10] less [11] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [13] less [14]
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15]
Load Forecast and Adjustments, MW:
Base Summer Peak Load (assuming normal weather)
less: Load Resources providing Responsive Reserves
less: Load Resources providing Non-Spinning Reserves
less: Load Resources providing ERCOT Contingency Reserve Service (ECRS)
less: Controllable Load Resources not included in other adjustments
less: Emergency Response Service (10- and 30-min ramp products)
less: TDSP Standard Offer Load Management Programs
less: Distribution Voltage Reduction
Firm Peak Load, MW
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | [1]: 3208; [4]: 3497; [7]: 3786; [10]: 4076; [13]: 4367
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
Installed Summer-rated Capacity, Thermal
Hydroelectric, Peak Average Capacity Contribution (80% of installed capacity)
Switchable Capacity
less: Switchable Capacity Unavailable to ERCOT
Available Mothballed Capacity (Units with reported return probabilities ≥ 75%)
Capacity from Private Use Networks
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
RMR Capacity to be under Contract
Capacity Pending Retirement
Operational Generation Capacity, Total
Non-Synchronous Ties (Based on average net import contribution during the summer 2023 EEA event)
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
Thermal Resources
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
Unconfirmed Planned Retirements
Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements
Total Capacity
Reserve Margin | bar: [1] to [9]
(Total Resources - Firm Load Forecast) / Firm Load Forecast
| Firm Peak Load plus New Contracted Loads Reported by TSPs | [1]: 2025; [3]: 2026; [5]: 2027; [7]: 2028; [9]: 2029
|  | #REF! |  | #REF! |  | #REF! |  | #REF! |  | #REF!

## Winter Summary
Report on the Capacity, Demand and Reserves in the ERCOT Region
Winter Summary: 2025-2029
|  | 2025 |  |  | 2026 |  |  | 2027 |  |  | 2028 |  |  | 2029
|  | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [1] less [2] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [4] less [5] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [7] less [8] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [10] less [11] | Peak Load Hour (HE ______) | Peak Net Load Hour (HE ______) | Difference [13] less [14]
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15]
Load Forecast and Adjustments, MW:
Base Summer Peak Load (assuming normal weather)
less: Load Resources providing Responsive Reserves
less: Load Resources providing Non-Spinning Reserves
less: Load Resources providing ERCOT Contingency Reserve Service (ECRS)
less: Controllable Load Resources not included in other adjustments
less: Emergency Response Service (10- and 30-min ramp products)
less: TDSP Standard Offer Load Management Programs
less: Distribution Voltage Reduction
Firm Peak Load, MW
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | [1]: 3208; [4]: 3497; [7]: 3786; [10]: 4076; [13]: 4367
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
Installed Summer-rated Capacity, Thermal
Hydroelectric, Peak Average Capacity Contribution (80% of installed capacity)
Switchable Capacity
less: Switchable Capacity Unavailable to ERCOT
Available Mothballed Capacity (Units with reported return probabilities ≥ 75%)
Capacity from Private Use Networks
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
RMR Capacity to be under Contract
Capacity Pending Retirement
Operational Generation Capacity, Total
Non-Synchronous Ties (Based on average net import contribution during the summer 2023 EEA event)
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
Thermal Resources
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
Coastal Wind
Panhandle Wind
Other Wind
Far West Solar Utility-Scale
West Solar Utility-Scale
Other Solar Utility-Scale
Energy Storage
Unconfirmed Planned Retirements
Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements
Total Capacity
Reserve Margin | bar: [1] to [9]
(Total Resources - Firm Load Forecast) / Firm Load Forecast
| Firm Peak Load plus New Contracted Loads Reported by TSPs | [1]: 2025; [3]: 2026; [5]: 2027; [7]: 2028; [9]: 2029
|  | #REF! |  | #REF! |  | #REF! |  | #REF! |  | #REF!

## Unit Details
NOTES
See the Acronym tab for terms associated with the Technology, Fuel, Status and CDR Resource Attribute columns below.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Resources Services (RIOO-RS) system.
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Seasonal Net Maximum Sustained Ratings, MW
UNIT NAME | INTERCONNECTION REQUEST NUMBER (INR) | UNIT CODE | TECHNOLOGY | FUEL | CDR STATUS | EXPECTED SERVICE RETURN | CDR RESOURCE ATTRIBUTE | COUNTY | ZONE | IN-SERVICE YEAR | INSTALLED CAPACITY (MW) | Spring |  |  |  |  | Summer |  |  |  |  | Fall |  |  |  |  | Winter
[12 empty] | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029 | 2025 | 2026 | 2027 | 2028 | 2029
COMANCHE PEAK U1 |  | CPSES_UNIT1 | NUCLEAR | NUCLEAR | OPER |  | CONV | SOMERVELL | NORTH | 1990
COLETO CREEK |  | COLETO_COLETOG1 | COAL | COAL | OPER |  | CONV | GOLIAD | SOUTH | 1980
ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | CC | GAS | OPER |  | CONV | BEXAR | SOUTH | 2000
ATKINS CTG 7 |  | ATKINS_ATKINSG7 | GT | GAS | OPER |  | CONV | BRAZOS | NORTH | 1973
DENTON ENERGY CENTER IC A |  | DEC_AGR_A | IC | GAS | OPER |  | CONV | DENTON | NORTH | 2018
REMY JADE POWER STATION | 23INR0339 |  | GT | GAS | PLAN |  | CONV | HARRIS | HOUSTON | 2024
NACOGDOCHES POWER |  | NACPW_UNIT1 | BIOMASS | LFG | OPER |  | CONV | NACOGDOCHES | NORTH | 2012
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | HYDRO | WAT | OPER |  | CONV | VAL VERDE | WEST | 1983
ARLINGTON OUTLET HYDROELECTRIC FACILITY |  | DG_OAKHL_1UNIT | HYDRO | WAT | OPER |  | SODG | TARRANT | NORTH | 1928
ANTELOPE IC 1 |  | AEEC_ANTLP_1 | IC | GAS | OPER |  | SWGR-AVA | HALE | PANHANDLE | 2016
ANTELOPE IC 1 |  | AEEC_ANTLP_1 | IC | GAS | OPER |  | SWGR-UNA | HALE | PANHANDLE | 2017
AGUAYO WIND U1 |  | AGUAYO_UNIT1 | WT | WIND-O | OPER |  | CONV | MILLS | NORTH | 2023
ANCHOR WIND U1 |  | ANCHOR_WIND1 | WT | WIND-O | OPER-SYN |  | CONV | CALLAHAN | WEST | 2024
AQUILLA LAKE 3 WIND | 22INR0499 |  | WT | WIND-O | PLAN |  | CONV | HILL | NORTH | 2027
ACACIA SOLAR |  | ACACIA_UNIT_1 | PV | SOLAR-O | OPER |  | CONV | PRESIDIO | WEST | 2012
AGATE SOLAR | 20INR0023 |  | PV | SOLAR-O | PLAN-INA |  | CONV | ELLIS | NORTH | 2020
ANCHOR BESS U1 |  | ANCHOR_BESS1 | BESS-LI | MWH | OPER |  | CONV | CALLAHAN | WEST | 2023
EAST TIE |  | DC_E | MWH | MWH | OPER |  | DC-TIE | FANNIN | NORTH
POWERLANE PLANT STG 1 |  | STEAM1A_STEAM_1 | ST | GAS | MOTH-SEA |  | CONV | HUNT | NORTH | 1966
BRANDON (LP&L) (DGR) (AS OF 10/2/2023) |  | BRANDON_UNIT1 | GT | GAS | MOTH-IND |  | CONV | LUBBOCK | PANHANDLE | 2021
CHISHOLM GRID |  | CHISMGRD_BES1 | BESS-LI | STORAGE | EXT-OUT | 13-17 Months | CONV | TARRANT | NORTH | 2021
PUN UNIT G1 |  | PUNUNIT_G1 | GT | GAS | OPER |  | PUN
PRIVATE USE NETWORK GEN-AGGREGATE |  |  | GT | GAS | OPER |  | PUN-AGR
EXT-OUT = Extended outage
OPER = Operational
OPER-SYN = Operational, synchronized only
MOTH-SEA = Seasonal mothballed (operating under a seasonal availability schedule)
MOTH-IND = Indefinitely mothballed
PLAN = Planned
PLAN-RPR = An existing unit being repowered
PLAN-INA = Planned-Inactive
CONV = Conventional generation unit
DC-TIE = Direct Current Asynchronous Tie
DGR = Distributed Generation Resource
PUN = Private Use Network generator(s)
PUN-AGR = Aggregate PUN resource, used for reporting the aggrgate PUN capacity contribution
SODG = Settlement Only Distribution Generator
SWGR-AVA = Switchable Generation Resource, available
SWGR-UNA = Switchable Generation Resource, Unavailable

## New CDR-Eligible Resources
New Planned Resources Eligible for CDR Report since the Last CDR Report, Published May 2024
5.6
The table below lists the planned resources that have met certain ERCOT Planning Guide criteria necessary for the resources to be included in this CDR report. These criteria are as follows:
Large Generators 1. For all resource types a signed Standard Generation Interconnection Agreement (SGIA) or other binding agreement (for municipally-owned utilities or electric cooperatives). 2. Air permits required by the Texas Commission on Environmental Quality (TCEQ) or notice that air permits are not required. 3. Submission of a "Declaration of Adequate Water Supplies" and proof that the resource has sufficient water supplies for electricity generation. Solar, wind, and Energy Storage Resources are exempt from this requirement.
Small Generators 1. ERCOT has determined that all data submission requirements for Resource Registration have been met and the generator is added to the ERCOT Network Operations Model. These requirement are met when the Small Generator has been issued a Model Ready Date.
Notes
Year of Projected Commercial Operations: The year is based on the projected Commercial Operations Date (COD) reported by the project developer. Planned projects with a "(DGR)" suffix indicate that the resource is a Distributed Generation Resource as defined in the ERCOT Nodal Protocols (Section 2.1). Projects ending with 'SLF' represent Battery Energy Storage Systems that are Self-Limiting Facilities (SLFs), where the MW capacities are reported as zero to reflect projects for which the battery system is sized to be less than the total nameplate capacity of all registered generators at the facility. Other generators at the facility typically include one or more inverter-based resources, such as solar.
5.6
| Project Name | GENERATION INTERCONNECTION PROJECT CODE | County | Fuel | Zone | Year of Projected Commercial Operations | Installed Capacity, MW
| TOTAL | [5 empty] | 0

## Capacity by Resource Type
Operational Resources, MW [1] | Installed Capacity Rating [2]
| [Time Periods?] |  | Scope of periods to report is still under consideration
Thermal
Natural Gas
Combined-cycle
Combustion Turbine
Internal Combustion Engine
Steam Turbine
Compressed Air Energy Storage
Coal
Nuclear
Renewable, Intermittent [6]
Solar
Far West
West
Other
Wind
Coastal
Panhandle
Other
Renewable, Other
Biomass
Hydroelectric [4]
Energy Storage, Available State of Charge
Batteries
Duration 1-hour or less |  | Range of duration categories is still under consideration
Duration 1-hour to 4-hour
Duration > 4-hour
Other
DC Tie Net Imports
Planned Resources [5]
Thermal
Natural Gas
Combined-cycle
Combustion Turbine
Internal Combustion Engine
Steam Turbine
Compressed Air Energy Storage
Diesel
Renewable, Intermittent [6]
Solar
Far West
West
Other
Wind
Coastal
Panhandle
Other
Energy Storage, Available State of Charge
Batteries
Other
Total Resources, MW
NOTES:
[1] Operational resources are those for which ERCOT has approved grid synchronization or full commercial operations. Unit level details for each resource category can be found in the Resource Details tab.
[2] Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. All gas-fired Private-Use Network (PUNs) units are reflected in the combined cycle fuel type row above.
[3] Expected Available Capacity for operational units accounts for thermal seasonal sustained capability ratings, hourly capacity contribution estimates for intermittent renewables, planned retirements, reductions due to co-located loads, unavailable Switchable Generation Resources (SWGRs), mothballed capacity, and expected Private Use Network (PUN) generator net exports to the grid. For planned projects, Expected Available Capacity is based on the maximum capacity reported by the developers and accounts for net changes due to repower or upgrade projects greater than one MW, and the established limits on the total MW Injection for designated Self-Limiting Facilities. Unit level details for each resource group above can be found in the Resource Details tab.
[4] Includes a small amount of hydro units that are considered intermittent resources (run-of-river DG hydro units).
[5] Planned resources are those for which ERCOT expects to be approved for grid synchronization or has been assigned a “Model Ready Date" (for Small Generators) by the first of the month.
[6] Wind and solar values represent the 50th percentile values from hourly synthetic output profiles used in the PRRM. See the Background tab for more information.

## Load-Resource Scenarios
EXAMPLE TABLE: ERCOT HAS NOT YET DECIDED ON THE CONTENTS AND LABELING FOR THIS TAB
Table 1: Summer Load and Resource Scenario | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2034 | 2035
Firm Peak Load, MW
Officer Letter Loads from Transmission Service Providers
Total Regional Transmission Plan Load
CDR-eligible Capacity, MW
Thermal
Inverter-Based Resources
Non-Synchronous Ties, MW
Planned Capacity with a signed IA but no financial security posted for interconnection facility construction
Total Capacity, MW
Planning Reserve Margin (%)
Table 2: Winter Load and Resource Scenario | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2034 | 2035
Firm Peak Load, MW
Officer Letter Loads from Transmission Service Providers
Total Regional Transmission Plan Load
CDR-eligible Capacity, MW
Thermal
Inverter-Based Resources
Non-Synchronous Ties, MW
Planned Capacity with a signed IA but no financial security posted for interconnection facility construction
Total Capacity, MW
Planning Reserve Margin (%)

## ELCCs
The follow table lists the wind, solar and battery energy storage Effective Load Carrying Capability (ELCC) values used for Planning Reserve Margin calculations. ELCC values are disaggregated by time periods: forecast year, season and reserve risk period (morning, afternoon and winter).
Effective Load Carrying Capabilities (ELCCs)
Year | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029 |  |  |  | 2025 |  |  |  | 2026 |  |  |  | 2027 |  |  |  | 2028 |  |  |  | 2029
Season | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall | Spring | Summer | Winter | Fall
Risk Period | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Morning | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Afternoon | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening | Evening
Resource Type
Solar - FarWest | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
Solar - West | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
Solar - Other | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
Wind - Panhandle | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
Wind - Coast | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
Wind - Other | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 1.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 2.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 3.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 4.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 5.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 6.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 7.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 8.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 9.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 10.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 11.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
BESS - 12.0 hr | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a | n/a | n/a |  | n/a
n/a - Not Applicable for non-winter morning reserve risk periods because the occurrence of loss-of-load events is expected to be negligible or non-existent.

## Acronyms
Acronyms
General
GIM = Generator Interconnection or Modification request
CDR = Capacity, Demand and Reserves Report
COD = Commercial Operations Date
ELCC = Effective Load Carrying Capability
HE = Hour Ending
INR = Interconnection Request Number
RIOO-IS = "Resource Integration and Ongoing Operations - Integration Services" system
RIOO-RS = "Resource Integration and Ongoing Operations - Registration Services" system
RTP = Regional Transmission Plan
TSP = Transmission Service Provider
CDR Status (For Unit Details table)
EXT-OUT = Extended outage
OPER = Operational
OPER-SYN = Operational, synchronized only
MOTH-SEA = Seasonal mothballed (Unit operating under a seasonal availability schedule)
MOTH-IND = Indefinitely mothballed
PLAN = Planned
PLAN-RPR = An existing unit being repowered and required to submit an interconnection request (See the Definitions tab for the CDR repower definition)
PLAN-INA = Planned-Inactive
CDR Resource Attributes (For Unit Details table)
CONV = Conventional generation resource (Unit that does not fall under the other CDR Attribute categories)
DC-TIE = Direct Current Asynchronous Tie
DGR = Distributed Generation Resource
PUN = Private Use Network generator(s)
PUN-AGR = Aggregate PUN resource, used for reporting the aggrgate PUN capacity contribution
SODG = Settlement Only Distribution Generator
SWGR-AVA = Switchable Generation Resource, available
SWGR-UNA = Switchable Generation Resource, Unavailable
Fuel Types (For Unit Details Table)
BIO = Biomass
COAL = Coal (bituminous, subbituminous, lignite)
GAS = National Gas
GEO = Geothermal
HYD = Hydrogen
NUC = Nuclear
OIL = Fuel Oil
OTH = Other
PET = Petcoke
SOL = Solar
WAT = Water
WIND-C = Wind from the Coastal wind region
WIND-P = Wind from the Panhandle wind region
WIND-O = Wind from the Other wind region
SOLAR-FW = Solar from the Far West CDR solar region
SOLAR-W = Solar from the West CDR solar region
SOLAR-O = Solar from the Other CDR solar region
Technology Types (For Unit Details table)
BA = Battery Energy Storage
CC = Combined-Cycle
CE = Compressed Air Energy Storage
CP = Concentrated Solar Power
EN = Energy Storage
FC = Fuel Cell
GT = Combustion (gas) Turbine, but not part of a Combined-Cycle
HY = Hydroelectric Turbine
IC = Internal Combustion Engine, eg. Reciprocating
OT = Other
PV = Photovoltaic Solar
ST = Steam Turbine other than Combined-Cycle
WT = Wind Turbine

## Definitions
Definitions
Available Mothballed Capacity based on Owner's Return Probability
Mothballed capacity with a return-to-service probability of 50% or greater for a given season of the year, as provided by its owner, constitutes available mothballed generation. Return probabilities for individual units are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Capacity Pending Retirement
Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2.
Contracted / Non-Contracted TSP Loads
Contracted TSP Load: A Load reported to ERCOT for which an interconnection agreements and/or Facility Extension Agreements (FEA) has been signed by the customer and Transmission Service Provider, and the customer share of costs for the extension of TSP facilities has been paid to the TSP. A contracted Load typically falls into the following general categories: crypto-mining, data centers, hydrogen/ammonia production, oil and gas production, and industrial/manufacturing. Non-contracted TSP Load: A Load (or Loads) for which an officer of a TSP has documented in a letter sent to ERCOT attesting that there is a high likelihood that the Load(s) will materialize. These prospective Loads are not associated with a signed interconnection agreement or FEA, and are therefore considered more speculative than Loads with a signed interconnection agreement or FEA.
Decommissioned Generation Resource
A Generation Resource for which a Resource Entity has submitted a Notification of Suspension of Operations (NSO) or a Notification of Change of Generation Resource Designation (NCGRD), for which ERCOT has declined to execute a Reliability Must-Run (RMR) Agreement, and which has been decommissioned and permanently retired.
Distribution Resource Types:
Settlement Only Distribution Generator (SODG)
A generator that is connected to the Distribution System with a rating of: (1) One MW or less that chooses to register as an SODG; or (2) Greater than one and up to ten MW that is capable of providing a net export to the ERCOT System and does not register as a Distribution Generation Resource (DGR). SODGs are settled for exported energy only, but may not participate in the Ancillary Services market, Reliability Unit Commitment (RUC), Security-Constrained Economic Dispatch (SCED), or make energy offers. SODGs are listed in the SummerCapacities and WinterCapacities with a DG_ prefix in the UNIT CODE column
Distribution Generation Resource (DGR)
A Generation Resource connected to the Distribution System that is either: (1) Greater than ten MW and not registered with the Public Utility Commission of Texas (PUCT) as a self-generator; or (2) Ten MW or less that chooses to register as a Generation Resource to participate in the ERCOT markets. DGRs must be registered with ERCOT in accordance with Planning Guide Section 6.8.2, Resource Registration Process, and will be modeled in ERCOT systems in accordance with Section 3.10.7.2, Modeling of Resources and Transmission Loads. DGRs are listed in the SummerCapacities and WinterCapacities tabs with a (DGR) suffix in the UNIT NAME column
Emergency Response Service
ERCOT uses the methodology specified in Protocol Section 3.2.6.2.1, Peak Load Estimate, to derive the ERS capacity forecast for future years. The Current Year for the calculations is defined as the latest year for which ERS has been procured. The ERS capacity amounts are grossed up by 2% to reflect avoided transmission line losses.
Energy Efficiency Program Savings Forecast
ERCOT's energy efficiency forecast uses the PUCT's annual verified energy efficiency program savings estimates as the starting point. (See the definition for verified energy efficiency program savings below.) Savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast. ERCOT computes the historical average annual verified savings, but excludes 2017 from the calculation due to Hurricane Harvey load impacts. (For prior forecasts, ERCOT used a formula based on the State energy efficiency goals in Utilities Code Section 39.905. Since the impacts of the goals were assumed to accumulate for just seven years from the time that the goals must be first met (2013), ERCOT no longer uses the goal-based forecasting approach.) Finally, ERCOT incorporates annual energy efficiency estimates from municipal utilities and electric cooperatives provided to the State Energy Conservation Office (SECO). Annual SECO report submission by these entities is required under S.B. No. 924. If annual reports for the previous calendar year are not available at the time the CDR is prepared, ERCOT incorporates report data for the most recently available reporting year. The energy efficiency capacity amounts are grossed up by a factor representing avoided transmission and distribution line losses. The factor is currently 1.076, reflecting 2% for avoided transmission losses and 5.6% for avoided distribution losses. The loss percentages are based on transmission and distribution loss factors posted to ERCOT's MIS website.
Energy Emergency Alert (EEA)
An ERCOT EEA declaration is made when operating reserves and system frequency drop below established severity levels (Levels 1, 2 and 3) and reserves are not projected to recover within 30 minutes unless certain actions are taken. An EEA declaration initiates an orderly, predetermined procedure for maximizing the use of available Resources, including the use of voluntary load reduction programs that are only available under EEA operations. Only under the most severe EEA level, would ERCOT direct Transmission and Distribution Service Providers to start shedding Load on a rotating basis in order to maintain system reliability and integrity. See Nodal Protocol Section 6.5.9.4, Energy Emergency Alert, for more details.
ERCOT Contingency Reserve Service (ECRS)
An Ancillary Service that provides operating reserves that is intended to: (a) Restore Responsive Reserve (RRS) within ten minutes of a frequency deviation that results in significant depletion of RRS by restoring frequency to its scheduled value to return the system to normal; (b) Provide energy or continued Load interruption to avoid or during the implementation of an Energy Emergency Alert (EEA); (c) Provide backup regulation; and (d) Be sustained at a specified level for two consecutive hours. ECRS was developed to address net load ramps and take advantage of Energy Storage Resources with maximum durations of at leat two hours.
Forecast Zone
The CDR report uses Forecast Zones to identify the geographical location of generation resources. Forecast Zones generally have the same boundaries as the 2003 Congestion Management Zones with the following exceptions: A) Panhandle Zone for resources in the Texas Panhandle counties and outside the 2003 Congestion Management Zones, and B) Coastal Zone for resources in 11 counties along the Texas Gulf Coast and formerly in the South Zone of the 2003 Congestion Management Zones. There are six Forecast Zones: Coastal, Houston, North, Panhandle, South, and West. Note that the CDR Forecast Zones are only used for resource adequacy reporting and are distinct from other ERCOT geographical reporting schemes used for planning, operational, or data reporting purposes.
Full Interconnection Study (FIS)
The set of studies conducted by a Transmission Service Provider (TSP) for the purpose of identifying any electric system improvements or enhancements required to reliably interconnect a new All-Inclusive Generation Resource consistent with the provisions of Planning Guide Section 5, Generation Resource Interconnection or Change Request. These studies may include steady-state studies, system protection (short-circuit) studies, dynamic and transient stability studies, facility studies, and sub-synchronous oscillation studies.
Inactive Projects
Per Planning Guide Section 5.7.6, a proposed Resource shall be given the status of “Inactive” if the Resource has not met the conditions for inclusion in the ERCOT planning models, as specified in Section 6.9, Addition of Proposed Generation to the Planning Models, within two years of the date on which ERCOT posts the final FIS studies for the Resource to the MIS Secure Area. A developer may also elect Inactive status and stop any interconnection studies in process at its own discretion. When an Inactive Resource subsequently meets the requirements of Section 6.9, it shall be added to the planning models and the status changed back to Planned. If a Resource has been Inactive for five years, ERCOT may cancel the project pursuant to Planning Guide Section 5.7.7, Cancellation of a Project Due to Failure to Comply with Requirements. Inactive planned projects are excluded from the CDR's reserve margin calculations.
Installed Capacity Rating
The installed capacity rating is the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. ERCOT uses Real Power Ratings that reflect the continous flow of power to loads (as opposed to reactive power, which is the power that flows back and forth between the power source and loads, and doesn't perform useful work.)
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include the summer Peak Load Season, June 1 through September 30.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 6, Ancillary Services. These Resources may provide the following Ancillary Services: Responsive Reserve Service, Non-Spinning Reserve Service, Replacement Reserve Service, and Regulation Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE). LR capacity has been grossed up by 2% to reflect avoided transmission line losses.
Mothballed Capacity
Capacity that is designated as mothballed by a generating unit's owner as described above, and which is not available for operations during the summer Peak Load Season (June, July, August and September) or winter Peak Load Season (December, January and February).
Peak Load Seasons
Summer months are June, July, August, and September; winter months are December, January, and February.
Private Use Networks
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).
Non-Synchronous Tie
Any non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Repower
For CDR reporting purposes, a repower is a an operational resource that needs to project for which one of the two following conditions apply: ● The Resource Entity is changing the inverter, turbine, generator, or power converter associated with a facility with an aggregate real power rating of ten MW or greater, unless the replacement is in-kind;Repowered Facility. See Planning Guide Section 5.2.1(1)(c)(ii). ● Increasing the aggregate nameplate capacity of a generator less than ten MW to ten MW or greater. See Planning Guide Section 5.2.1(1)(c)(v).
Signed SGIA (Standard Generation Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Generation Resource (SWGR)
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.
Synchronized but not Approved for Commerical Operations Capacity
These units have met requirements to Energize Equipment (Part 1 of Generator Commissioning Checklist): provided latest model data, verified Voltage Ride-Through capability and communication capabilities specified by ERCOT Operating Guides are in place. Output for these resources is not limited once they have passed a curtailment test and the project developer has submitted an attestation for the following plant controls: Automatic Voltage Regulator (AVR), Primary Frequency Response (PFR), Voltage Support Service (VSS), and Power System Stabilizer (PSS). A Synchronized unit get approved for Commerical Operations after the plant controls have been verified by ERCOT. More information on Synchronized units can be found in the Resource Interconnection Handbook pages 24 – 33.http://www.ercot.com/content/wcm/lists/168284/Resource_Interconnection_Handbook_v1.91_01082021.docx
TDSP Standard Offer Load Management Programs
For the May releases of the CDR report, ERCOT uses the megawatt amount of verified peak load capacity reductions, adjusted for avoided transmission losses, due to TDSP Standard Offcer load management programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. The reported amounts are for the most current reporting year, which is the calendar year prior to the year during which the May CDR is prepared. (For example, the May 2019 CDR report used verified program savings for the 2018 reporting year.) For the December CDR releases, ERCOT uses TDSP data received for the current load management program year, which is more timely than the verified savings estimates provided to the PUCT. The data obtained from the TDSPs reflect verified program performance for the summer based on testing, and is adjusted for avoided transmission losses.
Unconfirmed Retirement
A Generation Resource for which a public announcement of the intent to permanently shut the unit down has been released, but a Notice of Suspension of Operations for the unit has not been received by ERCOT. This is an informal definition that is not currently included in the Nodal Protocols or Other Binding Documents. The criteria for classifying a Generation Resource as an Unconfirmed Retirement include the following: a. A specific retirement date is cited in the announcement, or other timing information is given that indicates the unit will be unavailable as of June 1 of a CDR Reporting Year. b. The announcement, with follow-up inquiry by ERCOT, does not indicate that retirement timing is highly speculative.
Verified Energy Efficiency Program Savings
The total megawatt (MW) amount of verified peak load capacity reductions due to residential and commercial sector energy efficiency incentive programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. See Utilities Code Section 39.905. Note that savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast, but rather handled as a separate reporting line item.
Wind Peak Average Capacity Contribution
The seasonal net capacity rating of wind resources multiplied by the Seasonal Peak Average Capacity Percentage for the Coastal, Panhandle and Other CDR reporting regions.
Wind Seasonal Peak Average Capacity Percentage
The average wind capacity available for the summer and winter Peak Load Seasons for a CDR reporting region (Coastal, Panhandle, Other) divided by the installed capacity for the region, expressed as a percentage. Details for the derivation of the percentages are outlined in ERCOT Protocol Section 3.2.6.2.2 (see http://www.ercot.com/content/wcm/current_guides/53528/03-110119_Nodal.docx).
Wind Regions: Coastal, Panhandle, and Other
Wind Generation Resources (WGRs) are classified into regions based on the county that contains their Point of Interconnection (POI). The Coastal region is defined as the following counties along the Gulf Coast: Aransas, Brazoria, Calhoun, Cameron, Kenedy, Kleberg, Matagorda, Nueces, Refugio, San Patricio, and Willacy. The Panhandle region is defined as the following counties: Armstrong, Bailey, Briscoe, Carson, Castro, Childress, Cochran, Collingsworth, Crosby, Dallam, Deaf Smith, Dickens, Donley, Floyd, Gray, Hale, Hall, Hansford, Hartley, Hemphill, Hockley, Hutchinson, Lamb, Lipscomb, Lubbock, Moore, Motley, Ochiltree, Oldham, Parmer, Potter, Randall, Roberts, Sherman, Swisher, and Wheeler. The "Other" WInd Region consists of all other counties in the ERCOT Region. The assigned Wind Region for each WGR is indicated as "WIND-C," "WIND-P," or "WIND-O" in the Fuel columns of the summer/winter Capacities tabs.

## Wind-Solar Region Mapping
The tables below show what counties in the ERCOT region are mapped to the CDR Wind and Solar Regions.
Note: The CDR Wind and Solar Regions are intended to facilitate calculation of geographic-based Effective Load Carrying Capabilities (ELCCs) that represent wind and solar availabilities for Planning Reserve Margin calculation purposes. These are distinct from ERCOT zone definitions defined for other uses, such as the zones used for wind and solar production forecasting and reporting.
CDR Wind Region | County | CDR Solar Region | County
Coastal | Aransas | West | Andrews
Coastal | Brazoria | West | Archer
Coastal | Calhoun | West | Armstrong
Coastal | Cameron | West | Bailey
Coastal | Chambers | West | Baylor
Coastal | Galveston | West | Borden
Coastal | Jefferson | West | Brewster
Coastal | Kenedy | West | Briscoe
Coastal | Kleberg | West | Callahan
Coastal | Matagorda | West | Carson
Coastal | Nueces | West | Castro
Coastal | Orange | West | Childress
Coastal | Refugio | West | Clay
Coastal | San Patricio | West | Cochran
Coastal | Willacy | West | Coke
North | Anderson | West | Coleman
North | Angelina | West | Collingsworth
North | Bell | West | Concho
North | Bosque | West | Cottle
North | Bowie | West | Crane
North | Brazos | West | Crockett
North | Brown | West | Crosby
North | Camp | West | Culberson
North | Cass | West | Dallam
North | Cherokee | West | Dawson
North | Collin | West | Deaf Smith
North | Comanche | West | Dickens
North | Cooke | West | Donley
North | Coryell | West | Ector
North | Dallas | West | El Paso
North | Delta | West | Fisher
North | Denton | West | Floyd
North | Eastland | West | Foard
North | Ellis | West | Gaines
North | Erath | West | Garza
North | Falls | West | Glasscock
North | Fannin | West | Gray
North | Franklin | West | Hale
North | Freestone | West | Hall
North | Grayson | West | Hansford
North | Gregg | West | Hardeman
North | Grimes | West | Hartley
North | Hamilton | West | Haskell
North | Harrison | West | Hockley
North | Henderson | West | Howard
North | Hill | West | Hudspeth
North | Hood | West | Hutchinson
North | Hopkins | West | Irion
North | Houston | West | Jeff Davis
North | Hunt | West | Jones
North | Jack | West | Kent
North | Jasper | West | King
North | Johnson | West | Knox
North | Kaufman | West | Lamb
North | Lamar | West | Lipscomb
North | Lampasas | West | Loving
North | Leon | West | Lubbock
North | Limestone | West | Lynn
North | Madison | West | Martin
North | Marion | West | Menard
North | McLennan | West | Midland
North | Mills | West | Mitchell
North | Montague | West | Moore
North | Morris | West | Motley
North | Nacogdoches | West | Nolan
North | Navarro | West | Ochiltree
North | Newton | West | Oldham
North | Palo Pinto | West | Parmer
North | Panola | West | Pecos
North | Parker | West | Potter
North | Polk | West | Presidio
North | Rains | West | Randall
North | Red River | West | Reagan
North | Robertson | West | Reeves
North | Rockwall | West | Roberts
North | Rusk | West | Runnels
North | Sabine | West | Schleicher
North | San Augustine | FarWest | Scurry
North | San Jacinto | FarWest | Shackelford
North | San Saba | FarWest | Sherman
North | Shelby | FarWest | Sterling
North | Smith | FarWest | Stonewall
North | Somervell | FarWest | Sutton
North | Stephens | FarWest | Swisher
North | Tarrant | FarWest | Taylor
North | Titus | FarWest | Terrell
North | Trinity | FarWest | Terry
North | Tyler | FarWest | Throckmorton
North | Upshur | FarWest | Tom Green
North | Van Zandt | FarWest | Upton
North | Walker | FarWest | Val Verde
North | Wise | FarWest | Ward
North | Wood | FarWest | Wheeler
Panhandle | Armstrong | FarWest | Wichita
Panhandle | Bailey | FarWest | Winkler
Panhandle | Briscoe | FarWest | Yoakum
Panhandle | Carson | Other | Aransas
Panhandle | Castro | Other | Anderson
Panhandle | Childress | Other | Angelina
Panhandle | Cochran | Other | Atascosa
Panhandle | Collingsworth | Other | Austin
Panhandle | Crosby | Other | Bandera
Panhandle | Dallam | Other | Bastrop
Panhandle | Deaf Smith | Other | Bee
Panhandle | Dickens | Other | Bell
Panhandle | Donley | Other | Bexar
Panhandle | Floyd | Other | Blanco
Panhandle | Gray | Other | Bosque
Panhandle | Hale | Other | Bowie
Panhandle | Hall | Other | Brazoria
Panhandle | Hansford | Other | Brazos
Panhandle | Hartley | Other | Brooks
Panhandle | Hemphill | Other | Brown
Panhandle | Hockley | Other | Burleson
Panhandle | Hutchinson | Other | Burnet
Panhandle | Lamb | Other | Caldwell
Panhandle | Lipscomb | Other | Calhoun
Panhandle | Lubbock | Other | Cameron
Panhandle | Moore | Other | Camp
Panhandle | Motley | Other | Cass
Panhandle | Ochiltree | Other | Chambers
Panhandle | Oldham | Other | Cherokee
Panhandle | Parmer | Other | Collin
Panhandle | Potter | Other | Colorado
Panhandle | Randall | Other | Comal
Panhandle | Roberts | Other | Comanche
Panhandle | Sherman | Other | Cooke
Panhandle | Swisher | Other | Coryell
Panhandle | Wheeler | Other | Dallas
South | Atascosa | Other | Delta
South | Austin | Other | Denton
South | Bandera | Other | DeWitt
South | Bastrop | Other | Dimmit
South | Bee | Other | Duval
South | Bexar | Other | Eastland
South | Blanco | Other | Edwards
South | Brooks | Other | Ellis
South | Burleson | Other | Erath
South | Burnet | Other | Falls
South | Caldwell | Other | Fannin
South | Colorado | Other | Fayette
South | Comal | Other | Fort Bend
South | DeWitt | Other | Franklin
South | Dimmit | Other | Freestone
South | Duval | Other | Frio
South | Edwards | Other | Galveston
South | Fayette | Other | Gillespie
South | Fort Bend | Other | Goliad
South | Frio | Other | Gonzales
South | Gillespie | Other | Grayson
South | Goliad | Other | Gregg
South | Gonzales | Other | Grimes
South | Guadalupe | Other | Guadalupe
South | Hardin | Other | Hamilton
South | Harris | Other | Hardin
South | Hays | Other | Harris
South | Hidalgo | Other | Harrison
South | Jackson | Other | Hays
South | Jim Hogg | Other | Hemphill
South | Jim Wells | Other | Henderson
South | Karnes | Other | Hidalgo
South | Kendall | Other | Hill
South | Kerr | Other | Hood
South | Kimble | Other | Hopkins
South | Kinney | Other | Houston
South | La Salle | Other | Hunt
South | Lavaca | Other | Jack
South | Lee | Other | Jackson
South | Liberty | Other | Jasper
South | Live Oak | Other | Jefferson
South | Llano | Other | Jim Hogg
South | Mason | Other | Jim Wells
South | Maverick | Other | Johnson
South | McCulloch | Other | Karnes
South | McMullen | Other | Kaufman
South | Medina | Other | Kendall
South | Milam | Other | Kenedy
South | Montgomery | Other | Kerr
South | Real | Other | Kimble
South | Starr | Other | Kinney
South | Travis | Other | Kleberg
South | Uvalde | Other | La Salle
South | Victoria | Other | Lamar
South | Waller | Other | Lampasas
South | Washington | Other | Lavaca
South | Webb | Other | Lee
South | Wharton | Other | Leon
South | Williamson | Other | Liberty
South | Wilson | Other | Limestone
South | Zapata | Other | Live Oak
South | Zavala | Other | Llano
West | Andrews | Other | Madison
West | Archer | Other | Marion
West | Baylor | Other | Mason
West | Borden | Other | Matagorda
West | Brewster | Other | Maverick
West | Callahan | Other | McCulloch
West | Clay | Other | McLennan
West | Coke | Other | McMullen
West | Coleman | Other | Medina
West | Concho | Other | Milam
West | Cottle | Other | Mills
West | Crane | Other | Montague
West | Crockett | Other | Montgomery
West | Culberson | Other | Morris
West | Dawson | Other | Nacogdoches
West | Ector | Other | Navarro
West | El Paso | Other | Newton
West | Fisher | Other | Nueces
West | Foard | Other | Orange
West | Gaines | Other | Palo Pinto
West | Garza | Other | Panola
West | Glasscock | Other | Parker
West | Hardeman | Other | Polk
West | Haskell | Other | Rains
West | Howard | Other | Real
West | Hudspeth | Other | Red River
West | Irion | Other | Refugio
West | Jeff Davis | Other | Robertson
West | Jones | Other | Rockwall
West | Kent | Other | Rusk
West | King | Other | Sabine
West | Knox | Other | San Augustine
West | Loving | Other | San Jacinto
West | Lynn | Other | San Patricio
West | Martin | Other | San Saba
West | Menard | Other | Shelby
West | Midland | Other | Smith
West | Mitchell | Other | Somervell
West | Nolan | Other | Starr
West | Pecos | Other | Stephens
West | Presidio | Other | Tarrant
West | Reagan | Other | Titus
West | Reeves | Other | Travis
West | Runnels | Other | Trinity
West | Schleicher | Other | Tyler
West | Scurry | Other | Upshur
West | Shackelford | Other | Uvalde
West | Sterling | Other | Van Zandt
West | Stonewall | Other | Victoria
West | Sutton | Other | Walker
West | Taylor | Other | Waller
West | Terrell | Other | Washington
West | Terry | Other | Webb
West | Throckmorton | Other | Wharton
West | Tom Green | Other | Wilbarger
West | Upton | Other | Willacy
West | Val Verde | Other | Williamson
West | Ward | Other | Wilson
West | Wichita | Other | Wise
West | Wilbarger | Other | Wood
West | Winkler | Other | Young
West | Yoakum | Other | Zapata
West | Young | Other | Zavala

## Background
CDR Report Background
UNDER CONSTRUCTION
The main purpose of the CDR report is to provide forecasted Planning Reserve Margins by season and year. The Planning Reserve Margin represents the percentage of resource capacity, in excess of firm electricity demand, available to cover uncertainty in future demand, generator availability and new resource supply. Firm demand accounts for load reductions available through interruptible load programs controlled by ERCOT as well as incremental load reductions from rooftop solar systems not accounted for in the load forecast model. The methodologies used to develop Planning Reserve Margins and other elements of the CDR report are outlined in the ERCOT Nodal Protocols, Section 3.2.6 (See https://www.ercot.com/mktrules/nprotocols/current). ERCOT's load forecasts are based on normal weather conditions and determined by the methodology documents posted to the Load Forecast webpage, https://www.ercot.com/gridinfo/load/forecast.
Resource data comes from generation capacity developers (Interconnecting Entities, IEs) and owners as reported in ERCOT's Resource Integration and Ongoing Operations (RIOO) system, as well as other data collection mechanisms described in the ERCOT Nodal Protocols.
Effective Load Carrying Capabilities (ELCCs)
Note that the CDR is not intended for characterizing the risk of capacity scarcity conditions from a real-time operations perspective.