## Slide 1: Physical basics of low power operation of wind turbines
ERCOT IBRWG 11-15-24
Nick Miller

## Slide 2: Wind Turbine Components
Rotor
35 metric tons
77 meters diameter
Nacelle
52 metric tons
Tower
120+ metric tons
60 to 100 meters
Automobile (for scale)
Image source: GE Energy
GE 1.5 MW (c. 2002)
Generator
Gearbox
Hub
Aerodynamic
Torque
Electrical
Torque
Notes: A wind turbine generation system consists of a tower, a tower base standing on a foundation, the nacelle, and the rotor.
The rotor in modern units consists of three rotor blades which are mounted on the hub. The rotor blades must be marked with color above a defined unit height according to government regulations. This marking warns of the obstruction during the day. The unit may instead have white rotor blades and an additional so-called daytime obstruction marker (white flashing lights on the nacelle). The night marking is implemented with red flashing lights.

## Slide 3: Aerodynamic Lift – Bernoulli Effect
The air moves faster above the rotor blade than under it. This creates lift. All modern WTGSs are lift machines
Source: “Wind Energy Handbook”, Tony Burton et.al.; ISBN: 0471489972; 1st edition (November 15, 2001)
Bernoulli’s principle:
Increased speed of fluid flow results in a decrease of pressure
Resulting
air power
Fast air movement
Slow air movement
Vacuum
Horizontal
Angle of incidence
Positive pressure
Incoming air
The blade has to be moving through the air to get lift.
Lift in the right direction puts rotational torque on the drive train: Tmech
Notes: In modern wind turbine generation systems, lift machines are used almost exclusively. The wind doesn't drive the windwheels primarily because the rotor blades present drag to the wind, but due to the fact that the rotors use the lift force like airplane propellers. The rotor blades are shaped like airplane wings. If the wind flows over a rotor blade, then a lift force results, just as in an airplane. The air moves faster on the upper side of the rotor blade than on the lower.

## Slide 4: Conversion: Why 3 blades? What is Cp? Why variable speed?
  Rotor power: P = 1/2 cp rAvw3
    cp - rotor power coefficient
    r - air density
    A - rotor swept area
  Ideal cp = 0.593 (Betz factor) [think “Carnot efficiency for wind”]
    where V2 = 1/3 V1 (wind velocity slows by 2/3)
  Tip speed ratio: l = vt / vw
  cp = f(l)
    max for 3 blade rotor: cp = 0.47 at  = 7
    max for 2 blade rotor: cp = 0.45 at  = 10
    to operate at peak cp requires variable rotor speed
    2 blade machine will spin 30% faster, slightly lower cp
    diminishing returns for more than 3 blades
Source: “Windturbines: Fundamentals, Technologies, Application and Economics”, Erich Hau, ISBN: 3540570640; (April 30, 2000)
3 blades, maximum lift (pitch at minimum)
“Best” l
Rotation slows
Rotation speeds up
$
Family of representative Cp curves for 1, 2, 3 and 4 bladed wind turbines

## Slide 5: Wind Turbine Generator: allowing the turbine speed to vary
  Type 1 – Squirrel-cage induction generator
  Type 2 – Wound rotor induction generator with variable rotor resistance
  Type 3 – Doubly-fed asynchronous generator (DFIG)
  Type 4 – Full converter interface
  Type 5 – synchronous generator; mechanical slip

## Slide 6: Rotor speed basics are the same
Electrical
Torque, Te
Mechanical
Torque, Tm
Basic Notation:
J is the inertia of the entire drive-train in physical units
H is the inertia constant – it is scaled to the size of the machine.
A typical synchronous turbine-generator has an H of about 3.5 MW-sec/MW.

## Slide 7: Controlling Active Power: Models & Some History

## Slide 8: Controlling mechanical power (and torque): blade pitch and rotor speed
v
w
= wind speed
(User
-
provided function)
q
= blade pitch angle
P
mech
shaft power
(From Turbine Model)
w
= rotor speed
(From Turbine Model)
r,
A
r
,
K
b
(
constants
)
tip speed ratio, l = Kb (w / vw)
ideal Cp = 0.593
maximum Cp = 0.47 at l = 7 for 3 blade rotor
~20%: 5°
Rotation slows
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 1.0 December 2002
Family of Cp curves for one representative 3 bladed wind turbine.

## Slide 9: Turbine & Turbine Control
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
GE added the active power (frequency droop) control feature to the manual in 2008

## Slide 10: Turbine & Turbine Control
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Pmech vs Pelec balance: acceleration equations

## Slide 11: Turbine & Turbine Control
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Pmech vs Pelec balance: acceleration equations
Mechanical power: relationship between wind speed, rotor speed and blade pitch

## Slide 12: Turbine & Turbine Control
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Pmech vs Pelec balance: acceleration equations
Mechanical power: relationship between wind speed, rotor speed and blade pitch
Frequency response and curtailment command: issues upper power limit command

## Slide 13: Turbine & Turbine Control
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Pmech vs Pelec balance: acceleration equations
Mechanical power: relationship between wind speed, rotor speed and blade pitch
Frequency response and curtailment command: issues upper power limit command
Pitch control: satisfying speed and power objectives

## Slide 14: Over vs. Under-frequency Response
Speed (for synchronous machines)
Frequency (for wind plants)
100% (Normal Frequency)
Headroom
Plant
Power
Droop
Plant Power Dispatch
= actual production
Plant Power Maximum
= rating for synchronous plants
= available for wind plants)
Deadband
System short
of generation
System needs
Less power
“Droop “
Is the change in power output per change in frequency. But be careful: higher (more) droop means less aggressive response; lower slopes in the curve.
Can be asymmetric. Wind, and especially PV, can easily have different over- versus under-frequency droop characteristics.
From the GE 2008 manual:
“An example frequency response curve is shown
Points A through D set to meet the needs of the host grid.
The value of Pd should be greater than or equal to the minimum power.
The minimum power is nominally 0.20 pu of maximum farm output. .”
Technical Minimum
%5 curtailment (example)
MUCH lower over-frequency droop
Notes: Provide under-frequency response when you can and only pre-curtail if you have to
  ERCOT requires:
    Generators provide FR when there is headroom
    VER provides FR when curtailed for other reasons

## Slide 15: Power Curve Terminology
  Power output vs. wind speed
  at hub height – 10min average wind speeds
Example: official power curve for GE 1.5s
Image source: GE Energy
Roughly proportional to cube of wind speed in this range
Pitch out to maintain (maximum) power in this range

## Slide 16: Slight Curtailment (from ≤ rated wind speed)
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Credit: GE Vernova
DP~5%: ~1-2°, 0-2RPM
Fully Pitched in; slightly off Cp max for stability
Pbc = 95%
5% curtailment

## Slide 17: Slight Curtailment (from > rated wind speed)
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Credit: GE Vernova
Partially Pitched Out: a range of rotor speed and pitch will satisfy P objective
Pbc = 95%
5% curtailment

## Slide 18: Deep Curtailment (from ≤ rated wind speed)
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Credit: GE Vernova
DP~80%: ~20°
Dw ~70%: ~-14 RPM*
Full power
Pbc = 20%
80% curtailment
B
C
D
Rotor speed low
dP/dw much higher (~4x): much less stable speed/power control

## Slide 19: Why a technical minimum?
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008
Credit: GE Vernova
Cp needs to approach zero.
Lift approaches zero.
Blade speed approaches zero.
Pbc = 20%
80% curtailment
B
C
D

## Slide 20: It’s not that simple: this real physical equipment
Tower Nod
Tower twist
Blade
Flap
Blade
Twist
Blade
Edgewise
Shedding ALL the lift is ugly.
Every sailor knows not to stay “in irons”…. Not stable. Things break.

## Slide 21: “just pitch in!”
A blade for a 1.5MW turbine weights about 5 tons.
Turning it in fractions of seconds is mechanically challenging
Modeling of GE Wind Turbine-Generators for Grid Studies
Version 4.1 March 2008

## Slide 22: Increasing Power during very low wind conditions
A lower wind speeds, risk of stall if Pelec > Pmech is greatly increased.
Can not let the electrical control “get in front” of the pitch control much
Credit: GE Vernova
Dw ~70%: ~-14 RPM*
Reducing rotor speed rapidly reduces mechanical power
Pbc = 20%
80% curtailment
B
C
D
Rotor speed ~1/2 vs rated
dP/dw higher (~2x): much less inertial energy (~1/4) available

## Slide 23
Drawing down stored inertial energy:
Field Tests Results:
Test count:
8 m/s - 19 tests
10 m/s – 19 tests
14 m/s – 52 tests
WindINERTIA simulation models are openly available
Credit: GE Vernova
Only a few MW-sec of “spare” inertial energy available at 40% power.
We didn’t publish results for lower wind speeds. Available energy is very small: meaning that margin to stall is very small

## Slide 24: Conclusions
  Not possible to increase wind speed
  Slowing wind turbine reduces aerodynamic lift:
    Must avoid stall
  Must respect WTG component ratings:
    Mechanical loading
    Converter and generator electrical ratings
  Must respect other controls:
    Turbulence management
    Drive-train and tower loads management
  Active power control from very low power levels, whether due to deep curtailment or low wind speed is extremely challenging and subject to multiple physical and stability constraints.

## Slide 25: Thanks
nicholas.miller@hickoryledge.com