## Slide 1
Large Load Impact on GTCs
Yunzhi Cheng
ERCOT Operations Support
OWG Meeting
11/21/2024

## Slide 2: Large Load Impact on McCamey GTC Limits (GTLs)
Seven operational Large Loads (LLs) within McCamey GTC
  All connected to the 138kV system
  ~480MW (ERCOT approved) and included in the study
Dynamic model for LLs
  Composite load model “CMLD**U2” (motor + electronic) as provided by TSPs (LCRA & TNMP)
  In the QSA/GTC study, the electronic component of LL is assumed to be tripped with no reconnection once the voltage drops below 0.75pu, based on the observation in the recent actual events.
  In the recent McCamey GTC update, LLs start to have material impact to reduce GTC limits, as discussed in the ROS meeting on 9/9/2024: https://www.ercot.com/files/docs/2024/08/30/05-gtcupdate_ros_sep2024.pdf

## Slide 3: Large Load Impact on GTC Limits (GTLs)
G
Gen Stability Limit
= 500MW
GTL = 400MW
(LLs behind the GTC reduce power or disconnect during events)
GTC Interface
Pre-CTG flow: 400MW
Contingency
Post-CTG flow: 500MW
LL
(100MW)
G
Gen Stability Limit
= 500MW
GTL = 500MW
(without LL)
GTC Interface
Pre-CTG flow: 500MW
Contingency
Post-CTG flow: 500MW
LLs behind the GTC, if reduce power or disconnect during events, could lead to the lower GTC limits