## Slide 1: ERCOT ELCC Study Update
Kevin Carden

## Slide 2
Purpose

## Slide 3: Purpose
  To generate ELCCs by technology for 2 non-dispatchable technologies (e.g. 0-60GW Solar PV, 0-60GW Wind) and unlimited combinations of storage duration (X GW of 2 Hr Battery, Y GW of 4 Hr Battery, Z GW of 8 Hr Battery, etc.)
    Approach allows the user to define any given portfolio within a specified range
    This approach avoids intractable number of simulations to generate ELCCs

## Slide 4: Simulated Surface
  Simplify problem by leveraging SERVM to produce numerous LOLE Events for combinations of solar and wind at 0.1 LOLE, and utilizing out of model approach to establish storage value for each portfolio
 |  | Wind MW |  |  |  |  |  |  | 
 |  | 0 | 30,000 | 35,000 | 40,000 | 45,000 | 50,000 | 55,000 | 60,000
Solar MW | 0 |  |  |  |  |  |  |  | 
 | 20,000 |  |  |  |  |  |  |  | 
 | 25,000 |  |  |  |  |  |  |  | 
 | 30,000 |  |  |  |  |  |  |  | 
 | 35,000 |  |  |  |  |  |  |  | 
 | 40,000 |  |  |  |  |  |  |  | 
 | 45,000 |  |  |  |  |  |  |  | 
 | 50,000 |  |  |  |  |  |  |  | 
 | 55,000 |  |  |  |  |  |  |  | 
 | 60,000 |  |  |  |  |  |  |  | 

## Slide 5: Marginal Versus Average ELCC
Adapted from:
A review of the latest developments in ISO/RTOs across the country Zachary Ming, E3
https://www.naruc.org/core-sectors/electricity-energy/bulk-power-system/bulk-power-system-learning-modules/
For each solar and wind combination at 0.1 LOLE, and for each day with any EUE, the peak shaving capability of storage technology/ technologies can be calculated in Excel, then calibrated to SERVM simulations

## Slide 6: Risk Period Mapping
Risk periods were an output of the model; NOT a predefined input to the study
Winter risk did not shift between gross load and net load
Gross Load – Afternoon Risk Period – Average ELCC
Net Load – Evening Risk Period – Marginal ELCC

## Slide 7: ELCC Calculation Strategy
For each solar and wind combination at 0.1 LOLE*, and for each day with any EUE, the peak shaving capability of storage technology/ technologies can be calculated in Excel, then calibrated to SERVM simulations
*0.1 LOLE is a proxy for the reliability standard

## Slide 8: Storage ELCC Quantification
Storage is used to shave the net load peak in ascending order of storage duration
Peak shaved MW for each class of duration defines its average ELCC
Resource Class | Installed MW | Total Peak Shaved (MW) | Avg ELCC (%) | Avg Output During Energy Constrained Period (MW) | Marginal ELCC (%)
All Storage | 12,000 | 10,425 | - | 10,012 | -
2 Hour | 4,000 | 2,425 | 61% | 2,012 | 50%
8 Hour | 8,000 | 8,000 | 100% | 8,000 | 100%

## Slide 9: ELCC Visualization

## Slide 10: ELCC Calculations
Average ELCC
  Renewables
    Heuristic: reduction from gross load peak to net load peak
    Calculated as portfolio ELCC from SERVM simulations
    Technology ELCCs allocated via integration method
  Storage
    Heuristic: net load peak shaving
    Calculated as portfolio ELCC from analytical approach calibrated with SERVM simulations
    In the case of multiple durations of storage, value can be allocated amongst durations according to each tranche’s contribution to the reduction in net load peak
Marginal ELCC
  All technologies assessed at average output during storage constrained periods

## Slide 11: Expected Process Summary
Portfolio
User defines Solar, Wind, Battery Penetration
Event Lookup
LOL events are pulled from corresponding solar and wind penetration cases
Storage Value
For each LOL event day, storage performs peak shaving
Storage Class
For differing storage durations assessed, average ELCC is allocated based on reduction in net load peak
Solar + Wind
Renewable average ELCC is assessed from integration method from SERVM simulations
Aggregate
Reduction in net load peak for each duration is probability weighted into one annual and/or seasonal value
Marginal ELCC
Marginal ELCC is separately calculated for storage and renewables based on output during critical hours

## Slide 12: ELCC Calculator – Solar and Wind
Input CDR Capacity
Calculate Portfolio ELCC
Allocate Solar and Wind Contributions
Allocate Location-Specific Contributions
Interpolate
Integrate Marginal ELCCs

## Slide 13: ELCC Calculator – Solar/Wind - Summer
ELCC Type | Technology | 2025 ELCC (%)
Portfolio ELCC | Solar – West | 36.1%
 | Solar – Other | 27.2%
Marginal ELCC | Solar – West | 7.3%
 | Solar - Other | 5.5%
ELCC Type | Technology | 2025 ELCC (%)
Portfolio ELCC | Wind - Panhandle | 33.6%
 | Wind - Coast | 30.8%
 | Wind - Other | 15.7%
Marginal ELCC | Wind - Panhandle | 17.8%
 | Wind - Coast | 16.4%
 | Wind - Other | 8.3%

## Slide 14: ELCC Calculator – Solar/Wind - Winter
ELCC Type | Technology | 2025 ELCC (%)
Portfolio ELCC | Solar – West | 2.6%
 | Solar – Other | 2.0%
Marginal ELCC | Solar – West | 0.4%
 | Solar - Other | 0.3%
ELCC Type | Technology | 2025 ELCC (%)
Portfolio ELCC | Wind - Panhandle | 32.6%
 | Wind - Coast | 29.9%
 | Wind - Other | 15.2%
Marginal ELCC | Wind - Panhandle | 16.0%
 | Wind - Coast | 14.7%
 | Wind - Other | 7.5%

## Slide 15: ELCC Calculator – Storage
Input CDR Capacity
Apply SERVM Calibration
Dispatch Storage in Excel Against SERVM EUE Days

## Slide 16: SERVM/Excel Calibration
Penalty factors were established through calibration to apply to ELCCs obtained in the Excel workbook to better match the SERVM results
Penalty factors capture both additional benefits and constraints not in Excel model
  Benefits: ancillary service contribution, interactions with other resources
  Constraints: Starting SOC, outage effects on other resources

## Slide 17: Discussion and Observations
Approach avoids limitations seen in ELCC Surface approach (limited flexibility in selecting battery duration and combinations of batteries)
Calibrated to actual SERVM simulations
  Wide range of portfolios used for calibration to ensure fidelity
Desired portfolios not included within original renewable combinations require interpolation of results

## Slide 18
Results

## Slide 19: SERVM Simulation Results – Summer
Solar Marginal ELCCs
Wind Marginal ELCCs

## Slide 20: SERVM Simulation Results – Winter
Solar Marginal ELCCs
All Values <1%
Wind Marginal ELCCs

## Slide 21: SERVM Simulation Results – EUE Reports
Loss of load events are pulled from all solar and wind penetration cases
Perform storage peak shaving on loss of load events

## Slide 22: Locational Adjustments
Locational wind and solar ELCCs were calculated at 2025 penetrations for a 1 GW marginal unit
  Wind-C
  Wind-O
  Wind-P
  Solar-West
  Solar-Other

## Slide 23: ELCC Calculator – Inputs
Inputs based on CDR capacities
1 MW is included for any storage penetration/duration combination that is without capacity in the CDR

## Slide 24: ELCC Calculator – Outputs

## Slide 25: ELCC Calculator – Summer Results - Solar

## Slide 26: ELCC Calculator – Summer Results – Wind

## Slide 27: ELCC Calculator – Summer Results – Storage
All Storage ELCCs to be adjusted by EFORd

## Slide 28: ELCC Calculator – Winter Results - Solar

## Slide 29: ELCC Calculator – Winter Results – Wind

## Slide 30: ELCC Calculator – Winter Example – Storage
All Storage ELCCs to be adjusted by EFORd