## Slide 1: Reclosing Philosophy Near Inverter-Based Resources
Open Action Items | Responsible | Notes | Assigned
Develop guidance and recommendations for adjusting transmission reclosing and sectionalizing schemes that would significantly improve the IBR ride through probability and be reasonable to accomplish. Examples to look at would be no reclosing on 3 phase faults and adding current sensing directional intelligence on sectionalizing schemes to reduce number of times system is hit with faults. | IBRWG SPWG |  | 03/07/2024

## Slide 2: IEEE 2800
Continued…

## Slide 3: Reclosing Example
A
~
IBR
B
C
Station 2
D
E
Station 1
138 or 345 kV
Interconnection Line
Fault on IBR Tie Line:
CB A and CB C trip
Lead CB C Reclosing:
20 seconds open interval
Supervised reclose on a Dead Line only
Follow CB A Reclosing:
21 seconds open interval
F
~
Generator

## Slide 4: Reclosing Example
A
~
IBR
B
C
Station 2
D
E
Station 1
138 or 345 kV
Interconnection Line
F
~
Generator
Fault on Adjacent Line
CB A, CB B, and CB D all trip to isolate the fault
Ring Bus Reclosing:
Lead CB A – 11 seconds open interval, then supervised reclose on sync check
Follow CB B – Recloses one second after CB A on sync check
Station 1 Reclosing:
10 seconds open interval, then supervised reclose for the following conditions: sync check, Dead Line

## Slide 5: Reclosing Example
Sync Check Settings Example
Voltage Level
Angle difference
Slip Frequency
Number of Automatic Recloses
Time Delay between Automatic Recloses