## Slide 1
PDCWG Report to ROS
Chair: Kevin Bunch, EDF Trading North America
Vice Chair: Chad Mulholland, NRG
ROS
December 5th, 2024

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    NPRR 1257 and NOGRR251 Discussion
    Load Loss Analysis
    ERCOT Frequency Control Metrics and Regulation Reports
    TRE Report
    Analysis of Disturbances
  BAL-001-TRE-2 FMEs and IMFR
    0 FME in the month of October
  Frequency Control Report
  New Leadership for 2025

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 395 MW/0.1 Hz
IMFR Performance currently
1552.00 MW/0.1HZ

## Slide 5
Questions?

## Slide 6: Frequency Control Report
October 2024

## Slide 7: CPS1 Performance

## Slide 8: RMS1 Performance of ERCOT Frequency
Notes: 13.6 mHz on avg for October 2024

## Slide 9: Frequency Profile Analysis

## Slide 10: Time Error Corrections
Notes: We see significant time error accumulation towards the end of October. IRR unit operation (HSL jump) was one contributing factor and we adjusted ACE integral factor to correct the time error.

## Slide 11: ERCOT Total Energy
Notes: 39,558,950 MWh

## Slide 12: ERCOT Total Energy from Wind Generation
Notes:   9,476,562 MWH

## Slide 13: ERCOT % Energy from Wind Generation
Notes: 23.96% of total energy was provided by wind generation

## Slide 14: ERCOT Total Energy from Solar Generation
Notes: 4,825,974 MWh

## Slide 15: ERCOT % Energy from Solar Generation
Notes: 12.20% of total energy was provided by solar generation

## Slide 16: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in October 2024 = 155,165 MW*s on October 18th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
October Data:
Mean: 228,417 MW*s
Max: 299,001 MW*s on October 7th
Min: 155,165 MW*s on October 18th

## Slide 17: ERCOT Inertia Trend
Notes: Summary of ERCOT intertia for the previous 10 years. Lowest inertia this year was on March 29th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.