## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2019-03-20
3.1.2 | RPG Projects Backed out for lack of approval | Final | Tuesday, June 4,2019
3.1.2 | Recently approved RPG projects | Final | 2019-09-27
3.1.2 | Model updates/corrections | Final | 2019-12-09
3.1.3 | Transmission & Generation Outages | Final | 2019-04-29
3.1.5 | Temperatures used in Dynamic Rating Calculation | Final | 2019-01-08
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2019-09-30
3.2.2 | Renewable generation dispatch | Final | 2019-03-20
3.2.3 | Switchable Generation | Final | 2019-04-25
3.2.4 | DC tie modeling and dispatch | Final | 2019-03-20
3.2.5 | Reserve Requirements | Final | 2019-03-20
3.2.6 | Fuel Price assumptions | Final | 2019-05-30
Demand
3.3 | Load forecast (Reliability) 90/10 Forecast SSWG forecast Bounded Higher of calc RTP summer peak case forecast RTP Min load case forecast | Final | 2019-10-01
Other Studies
5.2.2 | Sensitivity Analysis | Final | 2019-11-18

## Start Cases
Date Last Updated: | 2019-03-20 | Back
Status | Final
SSWG case version | 18SSWG Update 1 Final - October 10, 2018
On Peak Cases
18SSWG_2021_SUM1_U1_Final_10102018.raw
18SSWG_2022_SUM1_U1_Final_10102018.raw
18SSWG_2024_SUM1_U1_Final_10102018.raw
18SSWG_2025_SUM1_U1_Final_10102018.raw
Off peak case
18SSWG_2022_MIN_U1_Final_10102018.raw

## Temp. for Dynamic Ratings
Date Last Updated: | 2019-01-08 | Back
Status | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 100
East | 105
Far West | 110
North Central | 110
North | 110
South Central | 105
South | 105
West | 105

## RPG Projects Backed out
Date Last Updated: | Tuesday, June 4,2019 |  | Back
Status | Final
Based on TPIT dated: | 2018-10-01
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
4822 | Bell County (BEC) - Gabriel (LCRA) 138 kV | Upgrade existing line | Bell County | Gabriel |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2008 | 2020-05-15 | 138 | Tier 3 |  |  |  | 121, 132, 3640, 3688, 7346, 13640 | Y | 12428 | 4822
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Cresson | Rocky Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5228 | 2020-05-15 | 138 | Tier 2 |  |  |  | 1881, 2202 | Y | 12436 | 4834
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Morgan Creek | McDonald Rd |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8360 | 2023-05-15 | 138 | Tier 3 |  |  |  | 1032, 1333 | Y | 13139 | 5436
5467 | Nacogdoches Southeast_HertyN 345kV Line | Establish a new 345kV Line | Nacogdoches Southeast | Herty North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6075 | 2020-05-15 | 345 | Tier 2 |  |  |  | 3119, 3321 | Y | 13171 | 5467
5475 | Lufkin Sw. Sta. - Herty North Sw. Sta. 345 kV Line | Construct a new 345 kV Line from Lufkin Sw. Sta. to Herty North Sw. Sta. | Lufkin Sw. Sta | Herty North Sw. Sta. |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6077 | 2020-05-15 | 345 | Tier 2 |  |  |  | 3117, 3321 | Y | 13180 | 5475
5490 | Liggett - Hackberry 138 kV DCKT Line | Upgrade existing Liggett - Hackberry 138 KV Double Ckt Line | Liggett | Hackberry |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 2020-05-15 | 138 | Tier 3 |  |  |  | 1996, 1997, 2001, 2002, 2010, 11923, 15002, 15020, 15021, 2388, 15025, 15026, 15045, 15046 | Y | 13228 | 5490
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station | South Royse |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4234 | 2020-05-15 | 345 | Tier 3 |  |  |  | 2469, 2470, 12471, 2437, 2467, 2471, 2478, 2702, 2710, 3103, 12702 | Y | 13251 | 5524
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station | Forney |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4114 | 2021-05-15 | 345 | Tier 3 |  |  |  | 2467, 2433, 2437, 2470, 2478, 150189, 2438, 12438 | Y | 13253 | 5526
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Shamburger North |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6083 | 2020-05-16 | 345 | Tier 3 |  |  |  | 3217, 3223, 3226, 2470, 3103, 3201, 3206 | Y | 13696 | 5981
6273 | Saginaw 345/138 kV autotransformer | Install new autotransformer and construct new 345 kV Line at Saginaw | SAGINAW | HICKS |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5274 | 2020-05-15 | 345 | Tier 2 |  |  |  | 2065, 2066, 2067, 11957, 11958, 1436, 1860, 1864, 1957, 2068, 2081, 2069, 2070, 11860 | Y | 14003 | 6273
6291 | Royse Sw. Sta. - Farmersville Sw. Sta. 345 kV DCKT Line | Rebuild existing 345 kV Line | Royse | Farmersville |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4255 | 2023-05-15 | 345 | Tier 3 |  |  |  | 1685, 2461, 2478 | Y | 14020 | 6291
6360 | Hicks - Roanoke 138 kV Line with Alliance 138 kV Sub | Construct new 138 kV Line | Hicks | Roanoke |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5253 | 2022-05-15 | 138 | Tier 2 |  |  |  | 1855, 1851, 1854, 2081, 2082 | Y | 14104 | 6360
6792 | Royse - Anna Tap 138 kV Line | Upgrade existing line | ROYSE | ANNA TAP |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4275 | 2020-05-15 | 138 | Tier 3 |  |  |  | 2472, 2527, 2707, 2374, 2528, 2708, 12527 | Y | 14590 | 6792
5466 | Herty North Sw. Sta. 345/138 kV Autotransformer | Install new 345/138 kV Autotransformer at Herty North Sw. Sta. | Herty North | Herty North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6076 | 2020-05-15 | 345 | Tier 3 |  |  |  | 3321, 3322, 3319 | Y | 13170 | 5466
5496 | Forney - Royse 345 kV Line | Upgrade existing Royse - Forney 345 kV Line | Royse | Forney |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4235 | 2020-05-15 | 345 | Tier 3 |  |  |  | 2437, 2467, 2470, 2474, 2478 | Y | 13234 | 5496
6288 | Watermill - Trinidad 345 kV Line | Install a breaker at Watermill Sw. on the Watermill - Trinidad 345 kV Line to establish double-breaker configuration | Watermill | Trinidad |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4249 | 2020-05-15 | 345 | Tier 3 |  |  |  | 2996, 2427, 2428, 2432 | Y | 14017 | 6288
7022 | Forney - Seagoville/Tri Corner 345 kV Double-circuit Line | Upgrade Forney - Seagoville/Tri Corner 345 kV Double-circuit Line | Forney | Tri Corner |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4227 | 2020-05-15 | 345 | Tier 3 |  |  |  | 2432, 2433, 2437, 3105 | Y | 14844 | 7022
6304 | Shamburger North - Shamburger 345 kV Line | Upgrade existing 345 kV Line | Shamburger North | Shamburger |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6085 | 2020-05-28 | 345 | Tier 3 |  |  |  | 3103, 3223 | Y | 14033 | 6304
5624 | Killeen Sw. Sta. 345/138 kV Autotransformer Replacement | Replace existing autotransformer | Killeen Sw. Sta. | Killeen Sw. Sta |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R797 | 2021-05-15 | 345 | Tier 3 |  |  |  | 3422, 3423, 13423 | Y | 13354 | 5624
5525 | Forney - Lake Hubbard 345 kV Line | Construct new 345 kV line | Forney | Lake Hubbard |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4233 | 2021-05-16 | 345 | Tier 2 |  |  |  | 2455, 2467 | Y | 13252 | 5525
5522 | Lake Hubbard 345/138 kV Switching Station | Construct new 345/138 kV switching station | Lake Hubbard |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4139 | 2021-05-17 | 345 | Tier 3 |  |  |  | 12455, 12456, 2401, 2402, 2455 | Y | 13249 | 5522
4829 | Hutto Sw. Sta. second 345/138 kV autotransformer | Install new autotransformer | Hutto |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R750 | 2022-05-15 | 345 | Tier 3 |  |  |  | 13660, 3696, 3666 | Y | 12435 | 4829
5479 | Trinidad_TriC_Watermill_345kV_DCKT | Upgrade existing DCKT line | Trinidad Sw. Sta | TriCorner/Watermill |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4045 | 2023-05-15 | 345 | Tier 3 |  |  |  | 2427, 2432, 3123, 3124 | Y | 13184 | 5479
7023 | Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line | Upgrade existing Hicks Sw. Sta. - Roanoke Sw. Sta. 345 kV Double-circuit Line | Hicks Sw. Sta. | Roanoke Sw. Sta. |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4227 | 2023-05-15 | 345 | Tier 3 |  |  |  | 1845, 1851, 1847, 1853, 2081 | Y | 14845 | 7023
17TPIT0031 | Elkton 345/138 kV autotransformer | Replace existing autotransformer | Elkton | Elkton |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6032-E | 2024-05-15 | 345 | Tier 3 |  |  |  | 3105, 3106, 29150 | Y | 10501 | 3155
4487 | Nueces Area 69kV Reinforcement | Expand and add new 138/69kV Auto at Valero East 69kV substation. Add 5th breaker to Champlin 138kV substation. Construct Champlin to Valero East 138kV Line. | Champlin | Valero East | 709 - 0879 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 2903 | 2020-10-30 01:00 | 138 | Tier 2 |  |  |  | 8528, 8476, 8859 | Y | 13570 | 4487

## Recently approved RPG project
Date Last Updated: | 2019-09-27 |  | Back
Status | Final
Project Name | TDSP | Approve Date
Bearkat - Added a new 27-miles 345-kV single circuit from Bearkat station to Longshore station | WETT | 2018-09-01
AEP Pecos County Project Modification | AEP | 2019-03-06
Naval Base - North Padre 69 KV Transmission Project | AEP | 2019-03-19
Burnet-Bertram-Andice Transmission Line Overhaul Project | PEC | 2019-04-19
Rising Star Area Improvements | BEPC | 2019-05-07
Beeville to Goliad 69 kV Line Rebuild Transmission Project | AEP | 2019-05-21
Dilley to Jourdanton 69 kV Transmission Project | AEP | 2019-06-18
Deepwater 345-138 kV Autotransformer Addition | CNP | 2019-07-01

## Model updates & corrections
Date Last Updated: | 2019-12-09 |  | Back
Status | Final
Model Corrections/Updates Made to the 2019 RTP Cases
Transmission Changes | TO | Case | [5 empty] | Comments
|  | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM
Carterville (79560) to Eisltap (79625) Ckt 1 138 kV Line Rating Change | Sharyland |  | X | X | X | X | X | Based on feedback from Sharyland
Amoco TNP (38650) to Grant Avenue TNP (39400) Ckt 1 69 kV Line Rating Change | TNMP |  | X | X | X | X | X | Based on feedback from TNMP
Added WETT Bernoulli station (POI for Edmondson Ranch Wind, already modeled in cases) | WETT |  | X | X | X | X | X | Based on WETT review and IDEV
Remove load bus at Coral (60434); Remove branch from Coral (60434) to Cryo (60721); Open line from Barrilla (6653) to Hoefs Road (6654) as normally open line. | AEP |  | X | X | X | X | X | Based on AEP feedback
Added load bus at Onyx (60435); Added 138kV branch from Sagarosa (60716) to Onyx (60435). | AEP |  | X | X | X | X | X | Based on AEP feedback
Added busses ANNOVA_LNG (5775) and PORTSOUTH (5776). Added two lines from ANNOVA_LNG (5775) to PORTSOUTH(5776). Reterminated the line from SCARBIDE4A (8337) to HIWAY511SUB8 (5767) into PORTSOUTH (5776). Added a new .1 mile line from SCARBIDE4A (8337) to PORTSOUTH (5776). | STEC |  |  |  |  | X | X | Notified by STEC
Applied AEP Mod project 45513 upgrading ratings on branch from Wormser4A (8295) to St_Nino4A (8653), and changing parameters on branch from Gateetp4A (8649) to ST_Nino4A (8653). | AEP |  |  |  |  | X | X | Tier 4 Mod project, confirmed by AEP
Added bus SCHOTTKY2A (8507), moved 30 MW load from THRRVRS2A (8400) to SCHOTTKY2A (8507), removed line from SUNNILAN2A (8406) to THRRVRS2A (8400) and added lines from SUNNILAN2A (8406) to SCHOTTKY2A (8507) to THRRVRS2A (8400). | AEP | X | X | X | X | X | X | Mod Project 44862 and notified by AEP
Multiple 138kV around the Culberson loop parameters and ratings update | ONCOR |  | X | X | X | X | X | Idevs provided by ONCOR
Transformer at Wickett 37980 rating A and B update | TNMP |  | X | X | X | X | X | Ratings are observed on later SSWG cases
Close the transformer AT1 at Twinbute 76011-76010 | LCRA |  | X | X | X | X | X | Confirmed with LCRA
TPIT Project number 5206 Brackettville to Escondido 138 kV Line was delayed from November of 2021 to October of 2022, therefore was removed from the 2022 SUM and 2022 MIN Cases. | AEP |  |  | X | X |  |  | Confirmed with AEP
Added recently energized DOW auto A2 at POI (42500) |  |  | X | X | X | X | X | Energization date occurred after the October 2018 SSWG cases were created
Changed Ben Davis - Murphy 138kV line ratings based on Oncor/Garland feedback | Oncor/Garland |  | X | X | X | X | X | Ratings updated based on TSP feedback
Added Deepwater 345-138 kV Autotransformer Addition | CNP |  | X | X | X | X | X | RPG approved project as of July 2019
Added AEP Brackettville to Escondido project to 2022 MIN and 2022 SUM cases | AEP |  |  | X | X |  |  | Feedback from AEP that CCN was recently approved and new in-service date is November 2021
Increased the rating of the 3WTX from bus 8383 to 8384 to 8380. | AEP | X | X | X | X | X | X | This change was made in NOMCR 55589_1 and is reflected in newer SSWG cases.
Increased the rating of the 138 kV line from bus 8980 to 80121. | AEP | X | X | X | X | X | X | This change was made in NOMCR 55511_1 and is reflected in newer SSWG cases.
Added bus 8644 between busses 8371 and 8758, and upgraded the lines connecting those busses. | AEP | X | X | X | X | X | X | This was due to the Tier 4 AEP Trade Zone Project, number 45346.
Opened Reynolds Sherwin (160182) and opened the line to that bus from LGE (160205) | AEP |  | X | X | X | X | X | Reynolds Sherwin plant is shut down - Confirmed with AEP
Updated ratings for the following 3-Winding transformers: Einstein 1 and 2, Telephone, Vealmore 1 and 2 | Oncor/Sharyland | X | X | X | X | X | X | Based on ONCOR provided idevs
Updated ratings for the following 3-Winding transformers: Laredo Plant, Palmito 1 and 2, Eagle Pass HVDC | AEP/Sharyland | X | X | X | X | X | X | Updated missing ratins based on Sharyland feedback and operational ratings
Added a second 345 kV circuit from Solstice to Bakersfield | AEP/LCRA |  |  | X |  |  |  | This line was inadvertently left out in the original October SSWG 2022 Min case only
Removed 138 kV circuit 2 from Fluvanna Wind to Dermott Switching Station, and modified ratings for the 138 kV line from Fluvanna Wind to Gopher Wind | ONCOR/Fluvanna Wind Energy 2 LLC |  | X | X | X | X | X | Based on ONCOR feedback, RARF, and 2019 October SSWG cases
Updated ratings for the Fowlerton (5709) 345 kV auto | STEC |  | X | X | X | X | X | Based on STEC feedback
Updated parameters for the Gilleland (9054) - Techridge (9191) 138 kV line | AEN |  | X | X | X | X | X | MOD Project 1029
Added Angstrom (80501) 345 kV bus, which taps the Whitepoint (8956) to South Texas Project (5915) 345 kV line, added 345 kV Grissom bus (8264) on the Lon Hill (8455) to Coleto Creek (8164) 345 kV line | AEP |  | X | X | X | X | X | Removed from the 2019 RTP Reliability Projects Spreadsheet as these additions are separate from the AEP Corpus North Shore Project
Updated ratings for the 138 kV line from Howard Lane to McNeil | AEN |  |  |  |  | X | X | MOD Project 48327 to reconductor Howard Lane to McNeil
Generation Changes | TO | Case | [5 empty] | Comments
|  | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM
Updated Lamesa Solar Unit 2 (133541) MaxMW | Oncor |  | X | X | X | X | X | Based on RARF data
Updated AIRCO GSU (110311-8144) limits | AEP |  | X | X | X | X | X | Based on AEP feedback
Added BVE Unit 3 (110773) reactive capability curve | CNP |  | X | X | X | X | X | Based on RARF data
Added WAP G8 (110018) reactive capability curve | CNP |  | X | X | X | X | X | Based on RARF data
Corrected minimum MVAR limits on Los Vientos units at busses 160741 and 160742 | AEP |  |  | X |  |  |  | Based on the other RTP cases and the February SSWG case
Corrected MVAR limits on Torcillas_W1 (161251), BBReezeW1 (161751), BBreezeW2 (161752), Eastray_5 (162151), and Chalupa_W1 (162251) | AEP TCC |  |  | X |  |  |  | Based on the other RTP cases and the February SSWG case
Increased generation of Formosa units already online on 69 kV network to provide N-1 security within the plant | Formosa |  |  | X |  |  |  | Based on discussions with Formosa
Update Trent unit 180051 Max Capability to 38.25MW (instead of 156MW from SSWG) | Oncor |  | X | X | X | X | X | Based on RARF data
Correct Sweet Wind units (180153) regulation bus to 71050 | LCRA |  | X | X | X | X | X | Based on the Generator Voltage Profile data
Moved TNMP capacitors from station 38045 to a new station 38035 | TNMP |  | X | X | X | X | X | Based on TNMP input
Opened Reynolds Sherwin (160181) | AEP |  | X | X | X | X | X | Based on AEP feedback - plant is shut down
Alpha Road -NorthH Line rating correction (MOD3065) | Oncor |  | X | X | X | X | X | Based on Oncor feedback.
Load Changes | TO | Case | [5 empty] | Comments
|  | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM
Removed Coral (60434) | AEP |  | X | X | X | X | X | Based on AEP feedback
Added Onyx (60435) | AEP |  | X | X | X | X | X | Based on AEP feedback
Added Annova LNG (5775) | STEC |  |  |  |  | X | X | Notified by STEC; 270 MW in 2023, 405 MW in 2025
Edited Shropshire (5555) | AEP |  | X |  | X | X | X | Removed industrial load and adjusted residential load
Removed Dupont Switch (8422) | AEP |  | X | X | X | X | X | Based on AEP feedback
Added Angstrom (80501) | AEP |  | X | X | X | X | X | Based on AEP feedback
Added Cheniere LNG (8580) | AEP |  |  | X | X | X | X | Based on AEP feedback
Opened Reynolds Sherwin (160182) | AEP |  | X | X | X | X | X | Reynolds Sherwin plant shut down which was serving this load.
Opened Hecker (8565) | AEP |  | X | X | X | X | X | Based on AEP feedback
Bus Voltage Changes | TO | Case | [5 empty] | Comments
|  | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM
Capacitor Bank Changes | TO | Case | [5 empty] | Comments
|  | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM
Opened Reynolds Sherwin (160182) | AEP |  | X | X | X | X | X | Based on AEP feedback
Phase Shifters | TO | Case | [5 empty] | Comments
|  | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM
Reversed the flow of the phase shifter at bus 8183. | AEP |  | X | X | X | X | X | The direction of power flow through this phase shifter caused violations. Reversing the direction (as it was in last year's cases) resolved the issues.
Closed the Nelson Sharpe phase shifter | AEP |  | X | X | X | X | X | The Nelson Sharpe phase shifter was shown as being bypassed. The operations model reflects that the phase shifter is in service.

## Transmission & Gen Outages
Date Last Updated: | 2019-04-29 |  |  |  |  | Back
Status | Final
Case
Outaged Element | Associated TO/RE | 2020 SUM | 2021 SUM | 2022 MIN | 2022 SUM | 2024 SUM | 2025 SUM | Notes
Decker Unit #1 (170151) | AEN |  | X | X | X | X | X | Notified by AEN, and based on AEN's public announcement https://www.austintexas.gov/edims/document.cfm?id=317748
Decker Unit #2 (170152) | AEN |  |  | X | X | X | X | Notified by AEN, and based on AEN's public announcement https://www.austintexas.gov/edims/document.cfm?id=317748
OKLAUNION U1 | AEP | X | X | X | X | X | X | Based on AEP's public announcement https://aep.com/Assets/docs/investors/AnnualReportsProxies/docs/18annrep/2018AnnualReportAppendixAtoProxy.pdf
Some transmission outages collected by ERCOT Market Notice "M-A011419-01 Request for known outage(s) with a duration of at least six months to address NERC TPL-001-4" were also incorporated in applicable cases. The outage information is available on ERCOT MIS TSP Certified Area.

## Gen add, ret. and mothball
Date Last Updated: | 2019-09-30 |  |  |  |  | Back
Status | Final
Based on GIS report dated: | 2019-01-19
Based on NSO and Notice of Change of Generation Resource Designation received by
New generators that met PG 6.9 requirements
GINR Reference Number | Project Name | County | Projected Date | Fuel | MW For Grid | Changes From Last Report | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2020 | 2021 | 2022MIN | 2022 | 2023 | 2024 | 2025 | Comments
18INR0055 | Long Draw Solar | Borden | 2020-06-30 | SOL | 225 |  | 2019-02-28 | X | X | X | X | X | X | X | Per WETT review and idev
18INR0014 | Karankawa Wind | San Patricio | 2019-12-31 | WIN | 200 |  | 2017-11-30 | X | X | X | X | X | X | X | Simple model added during case conditioning
18INR0045 | Misae Solar | Childress | 2019-11-29 | SOL | 240.8 |  | 2019-01-28 | X | X | X | X | X | X | X | Simple model added during case conditioning
19INR0074 | Karankawa 2 Wind | San Patricio | 2019-12-31 | WIN | 200 |  | 2018-03-02 | X | X | X | X | X | X | X | Simple model added during case conditioning
19INR0184 | Oxy Solar | Ector | 2019-07-15 | SOL | 16.2 |  | 2019-01-30 | X | X | X | X | X | X | X | Simple model added during case conditioning
20INR0042 | Chalupa Wind | Cameron | 2020-12-21 | WIN | 174 |  | 2018-10-18 |  | X | X | X | X | X | X | Simple model added during case conditioning
12INR0055 | S_Hills Wind | Baylor | 2019-04-01 | WIN | 30.24 |  | 2018-10-04 | X | X | X | X | X | X | X | Added during case conditioning
17INR0037 | Palmas Altas Wind | Cameron | 2020-01-10 | WIN | 144.9 | COD | 2018-10-04 | X | X | X | X | X | X | X | Added during case conditioning
13INR0026 | Canadian Breaks Wind | Oldham | 2019-09-13 | WIN | 210 |  | 2018-09-04 | X | X | X | X | X | X | X | Added during case conditioning
16INR0076 | Hudson (Ineos/Brazoria) | Brazoria | 2019-01-31 | GAS | 96 |  | 2018-10-09 | X | X | X | X | X | X | X | Added during case conditioning
16INR0111 | Las Lomas Wind | Starr | 2019-12-31 | WIN | 200 |  | 2019-01-29 | X | X | X | X | X | X | X | Simple model added during case conditioning
16INR0114 | Upton Solar | Upton | 2020-05-31 | SOL | 104.56 |  | 2018-12-14 | X | X | X | X | X | X | X | Simple model added during case conditioning
18INR0018 | Peyton Creek Wind | Matagorda | 2019-12-01 | WIN | 151.2 |  | 2018-03-19 | X | X | X | X | X | X | X | Added during case conditioning
18INR0059 | Raymond Wind | Willacy | 2020-06-30 | WIN | 201.6 | COD | 2018-10-17 | X | X | X | X | X | X | X | Simple model added during case conditioning
19INR0019 | Foard City Wind | Foard | 2019-09-01 | WIN | 350 |  | 2018-06-22 | X | X | X | X | X | X | X | Added during case conditioning
19INR0029 | Phoebe Solar | Winkler | 2019-09-01 | SOL | 250 |  | 2018-03-05 | X | X | X | X | X | X | X | Added during case conditioning
19INR0045 | Rayos Del Sol | Cameron | 2020-12-31 | SOL | 150 | SFS/NtP | 2019-01-23 | X | X | X | X | X | X | X | Simple model added during case conditioning
19INR0083 | Oberon Solar | Ector | 2019-12-15 | SOL | 180 |  | 2018-11-28 | X | X | X | X | X | X | X | Added during case conditioning
19INR0112 | Cranel Wind | Refugio | 2019-12-31 | WIN | 220 |  | 2018-10-12 | X | X | X | X | X | X | X | Simple model added during case conditioning
20INR0011 | Ranchero Wind | Crockett | 2019-06-04 | WIN | 300 |  | 2018-08-03 | X | X | X | X | X | X | X | Added during case conditioning
21INR0026 | Juno Solar | Borden | 2021-05-15 | SOL | 495 |  | 2019-01-23 |  | X | X | X | X | X | X | Simple model added during case conditioning
21INR0032 | Juno Storage | Borden | 2021-05-15 | OTH | 495 |  | 2019-01-23 |  | X | X | X | X | X | X | Simple model added during case conditioning
Retired units
Unit Name | MW For Grid | 2020 | 2021 | 2022MIN | 2022 | 2023 | 2024 | 2025 | Comments
Mothballed units
Unit Name | MW For Grid | 2020 | 2021 | 2022MIN | 2022 | 2023 | 2024 | 2025 | Comments
SPENCER STG U4 | 57 | X | X | X | X | X | X | X | Per Dec 2018 CDR: Seasonal mothball unit, taken offline for reliability studies
SPENCER STG U5 | 61 | X | X | X | X | X | X | X | Per Dec 2018 CDR: Seasonal mothball unit, taken offline for reliability studies
J T DEELY U1 | 420 | X | X | X | X | X | X | X | Per Dec 2018 CDR as of 12/31/2018
J T DEELY U2 | 420 | X | X | X | X | X | X | X | Per Dec 2018 CDR as of 12/31/2018
S R BERTRON U1 | 112 | X | X | X | X | X | X | X | Per Dec 2018 CDR since 5/15/2013
S R BERTRON U2 | 168 | X | X | X | X | X | X | X | Per Dec 2018 CDR since 5/15/2013
NOTE: Simple model Settlement Only Distributed Generators (SODGs) were added to reflect those currently operational. Battery models were also added to reflect those currently in the Operations model.

## Renewable Generation Dispatch
Date Last Updated: | 2019-03-20 |  | Back
Status | Final
Solar
Information obtained from the spreadsheet "CDR Summer PeakAveSolarCapacityPercentages 10 21 2018" posted on the ERCOT website under Resource Adequacy.
* SOLARPEAKPCT Values | 74%
* The methodology for calculating SOLARPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Wind
Information obtained from the spreadsheet "CDR Summer PeakAveWindCapacityPercentages 10 21 2018" posted on the ERCOT website under Resource Adequacy.
Outside Study Region
WINDPEAKPCT Values *
Summer, Non-Coastal | Summer, Coastal
15% | 58%
* The methodology for calculating WINDPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See:http://www.ercot.com/content/wcm/current_guides/53528/03-090118_Nodal.docx
Inside Study Region
Study Region | Weather Zone | Average Capacity Factor (15th Percentile)
EC | COAST | 13.63%
NNC | NORTH | 6.689%
NNC | NORTH_CE | 3.073%
SSC | SOUTHERN | 19.5%
WFW | WEST | 4.331%
WFW | FAR WEST | 4.81%
Hydro
Unit specific generation MW dispatch modeled using CDR methodology which is based on historical Settlements HSL dispatch levels during the top 20 load hours of the last three years.
AMI_AMISTAG1 (H1) | 18.7333
AMI_AMISTAG2 (H2) | 28.834
AUS_AUSTING1 (H1) | 8
AUS_AUSTING1 (H2) | 8.5233
BUC_BUCHANG1 (H1) | 16
BUC_BUCHANG2 (H2) | 16
BUC_BUCHANG3 (H3) | 17
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 29.3333
DND_DENISOG2 (H2) | 40
EA_EAGLE_HY1 (H1) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H3) | 0
FAL_FALCONG1 (H1) | 7.091
FAL_FALCONG2 (H2) | 8.1667
FAL_FALCONG3 (H3) | 7.9833
INKS_INKS_G1 (H1) | 13.3433
MAR_MARBFAG1 (H1) | 19.8122
MAR_MARBFAG2 (H2) | 19.271
MAR_MARSFOG1 (H1) | 34.7333
MAR_MARSFOG2 (H2) | 35.83
MAR_MARSFOG3 (H3) | 29
WIR_WIRTZ_G1 (H1) | 28.58
WIR_WIRTZ_G2 (H2) | 29
WND_WHITNEY1 (H1) | 19.65
WND_WHITNEY2 (H2) | 19.65
Wind (Min Case)
Non-Coastal | Coastal
48.63% | 32.24%

## Switchable Generation
Date Last Updated: | 2019-04-25 |  |  |  |  | Back
Status | Final
Operational Resources (Switchable)
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2017 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2017 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | WEST | 2017 | 0 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2017 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2017 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
TENASKA GATEWAY STATION STG 4* | FTR_FTR_G4 | GRIMES | GAS | NORTH | 2016 | 400 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | -789.2 | -843.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8
*Note: the Tensaka Frontier is going to keep 300 MW switched out of the 400MW STG4 unit for year 2019 and 2020

## DC Tie modeling & dispatch
Date Last Updated: | 2019-03-20 |  | Back
Status | Final
Reliability Analysis
DC Tie dispatch - Summer peak conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L* | 100 | Export
DC_R* | 300 | Export
DC_S* | 30 | Export
* In the events that thermal overloads are resolved by curtialing the DC Tie exports, the events and the curtailed amounts will be documented.

## Reserve Requirement
Date Last Updated: | 2019-03-20 | Back
Status | Final
Reliabity Cases | 2800 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage.

## Fuel Price Assumptions
Date Last Updated: | 2019-05-30 |  |  |  |  | Back
Status | Final
Source | 2019 EIA AEO High Oil and Gas Resource and Technology
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2019 | 3.1874 | 2.6809 | 2.6069 | 2.6802 | 2.7585 | 2.9308 | 2.9809 | 2.9726 | 3.02 | 2.9701 | 2.9982 | 3.0113 | 2.8998
2020 | 3.1882 | 2.6816 | 2.6076 | 2.6809 | 2.7592 | 2.9315 | 2.9816 | 2.9733 | 3.0208 | 2.9709 | 2.9989 | 3.0121 | 2.9006
2021 | 3.0904 | 2.5994 | 2.5276 | 2.5986 | 2.6745 | 2.8416 | 2.8902 | 2.8821 | 2.9281 | 2.8797 | 2.9069 | 2.9197 | 2.8116
2022 | 3.1036 | 2.6104 | 2.5384 | 2.6097 | 2.6859 | 2.8537 | 2.9025 | 2.8944 | 2.9406 | 2.892 | 2.9193 | 2.9322 | 2.8236
2023 | 3.2676 | 2.7483 | 2.6725 | 2.7476 | 2.8278 | 3.0045 | 3.0558 | 3.0473 | 3.096 | 3.0448 | 3.0736 | 3.0871 | 2.9727
2024 | 3.5088 | 2.9512 | 2.8698 | 2.9504 | 3.0366 | 3.2263 | 3.2814 | 3.2723 | 3.3245 | 3.2696 | 3.3005 | 3.315 | 3.1922
2025 | 3.8109 | 3.2053 | 3.1168 | 3.2044 | 3.298 | 3.504 | 3.564 | 3.554 | 3.6107 | 3.5511 | 3.5846 | 3.6004 | 3.467

## Reliability Case-Load Forecast
Date Last Updated | 2019-10-01 |  |  |  |  | Back
Status | Final
SSWG Load in 18SSWG dated 10/10/2018 less Self-Served (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | NCP Total
2020 | 24007.61 | 2872.98 | 5652.73 | 1630.25 | 25165.26 | 13267.71 | 6316.09 | 2195.41 | 81108.04
2021 | 24437.26 | 2884.56 | 6050 | 2055.26 | 25543.47 | 13545.13 | 6490.32 | 2209.63 | 83215.63
2022 | 24617.03 | 2902.64 | 6261.26 | 2063.56 | 25871.79 | 13801.63 | 6724.95 | 2220.7 | 84463.56
2023 | 24768.15 | 2940.59 | 6403.64 | 2069.35 | 26271.54 | 14010.19 | 7082.37 | 2237.19 | 85783.02
2024 | 24909.44 | 2966.09 | 6510.43 | 2083.07 | 26648.3 | 14074.45 | 7203.68 | 2244.21 | 86639.67
2025 | 25088.89 | 3002.34 | 6625.33 | 2099.94 | 27061.37 | 14440.11 | 7302.1 | 2267.32 | 87887.4
ERCOT 90th Percentile Load forecast for RTP (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | NCP Total
2020 | 22619.5774 | 3019.3698 | 4422.7292 | 1898.2904 | 26996.5385 | 13693.0359 | 6337.4399 | 2323.728 | 81310.709
2021 | 23113.4087 | 3043.6682 | 4693.8904 | 2398.7536 | 27292.3592 | 13931.8294 | 6513.269 | 2384.1692 | 83371.3477
2022 | 23612.6987 | 3076.3889 | 4966.9461 | 2407.7016 | 27602.1745 | 14184.6062 | 6698.4853 | 2449.0917 | 84998.0929
2023 | 24115.6376 | 3103.7174 | 5239.2351 | 2416.7842 | 27916.6469 | 14439.2303 | 6892.5267 | 2515.5606 | 86639.3388
2024 | 24612.2704 | 3130.9887 | 5504.3736 | 2425.6422 | 28225.5662 | 14687.1449 | 7083.6975 | 2579.7185 | 88249.4021
2025 | 25106.1989 | 3156.8907 | 5770.996 | 2434.3861 | 28534.7059 | 14931.9271 | 7276.0028 | 2643.1879 | 89854.2955
2019 RTP final load forecast based on on 5% boundary threshold (MW) (Far West with 7.5% boundary threshold and also adjusted based on ERCOT load review results)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | Total
2020 | - | - | - | - | - | - | - | - | -
2021 | 27781.04 | 2928 | 5689.98 | 2220.77 | 26750 | 13658.16 | 7126 | 2430.85 | 88584.8
2022 | 28297.47 | 2945.73 | 5865.39 | 2229.02 | 27041 | 13905.98 | 7456 | 2493.27 | 90233.86
2023 | - | - | - | - | - | - | - | - | -
2024 | 28864.58 | 3009.12 | 6151.43 | 2245.56 | 27652 | 14398.72 | 7991 | 2619.09 | 92931.5
2025 | 29045.54 | 3045.28 | 6256.29 | 2253.67 | 27955 | 14638.7 | 8232 | 2680.13 | 94106.61
2019 RTP final load forecast for Off-Peak Case (MW) (based on 2022 SSWG Min Case)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | Total
2022 | 13799.54 | 1104.99 | 2983.91 | 765.97 | 8366 | 4849.83 | 3353 | 1086.72 | 36309.96

## Sensitivity Analysis
Date Last Updated: | 2019-11-18 |  |  |  |  | Back
Status | Final
Sensitivity 1: | No-Wind-No-Hydro Sensitivity for Summer Peak Conditions
Year | Wind Capacity Unavailable in the sensititivy cases |  |  |  | Hydro Capacity Unavailable in the sensititivy cases
| EC | NNC | WFW | SSC | EC | NNC | WFW | SSC
2021 | 21 | 588 | 564 | 1341 | - | 108 | 110 | 236
2024 | 21 | 588 | 576 | 1341 | - | 108 | 110 | 236
Sensitivity 2: | Wind Capacity Unavailable in the sensititivy cases EC: High-Wind-Low-Load Sensitivity for Off-Peak Conditions
Case | Wind Capacity Unavailable in the sensititivy cases EC: ERCOT Load (MW); Wind Capacity Unavailable in the sensititivy cases NNC: DC Tie Export* (MW); Wind Capacity Unavailable in the sensititivy cases WFW: Wind Output (MW)
|  |  | South | Coastal | West | North | Panhandle | Total
2022 Min | 36311 | -340 | 1409 | 1376 | 6043 | 650 | 2575 | 12053
2022 HWLL | 37159 | 1250 | 2695 | 4014 | 12919 | 1197 | 5058 | 25883
* negative sign indicating DC tie import.