## Index
RTP Scope Section Number | Input Assumption | Status | Date
Transmission Topology
3.1.1 | Start Cases | Final | 2018-03-20
3.1.5 | Temperatures used in Dynamic Rating Calculation | Final | 2018-03-20
3.1.2 | RPG Projects Backed out for lack of approval | Final | 2018-03-20
3.1.2 | Recently approved RPG projects | Final | 2018-03-20
3.1.2 | Model updates/corrections | Final | 2018-11-16
3.1.3 | Transmission & Generation Outages | Final | 2018-03-20
| CMP modeled in RTP | Final | 2018-09-28
Generation
3.2.1 | Generation Additions, Retirements and Mothballs | Final | 2018-09-28
3.2.2 | Renewable generation dispatch | Final | 2018-03-20
3.2.3 | Switchable Generation | Final | Tuesday, March 20, 2018
3.2.4 | DC tie modeling and dispatch | Final | 2018-03-20
3.2.5 | Reserve Requirements | Final | 2018-03-20
3.2.6 | Fuel Price assumptions | Final | 2018-03-14
Demand
3.3 | Load forecast (Reliability) 90/10 Forecast SSWG forecast Bounded Higher of calc RTP summer peak case forecast RTP Min load case forecast | Final | 2018-11-16
Other Studies
5.2.2 | Sensitivity Analysis | Final | 2018-11-13

## Start Cases
Date Last Updated: | 2018-03-20 | Back
Status | Final
SSWG case version | 17SSWG Update 1 Final - October 12, 2017
On Peak Cases
17SSWG_2020_SUM1_U1_Final_10122017.raw
17SSWG_2021_SUM1_U1_Final_10122017.raw
17SSWG_2023_SUM1_U1_Final_10122017.raw
17SSWG_2024_SUM1_U1_Final_10122017.raw
Off peak case
17SSWG_2021_MIN_U1_Final_10122017.raw

## Temp. for Dynamic Ratings
Date Last Updated: | 2018-03-20 | Back
Status | Final
Weather Zone | 90th Percentile Temperature (degree F)
Coast | 102.44
East | 106.25
Far West | 110.405
North Central | 108.35
North | 109
South Central | 105.45
South | 103.98
West | 107.304

## RPG Projects Backed out
Date Last Updated: | 2018-03-20 |  | Back
Status | Final
Based on TPIT dated: | 2017-10-01
ERCOT Project Number | Project Title | Project Description | "from" Location | "to" Location | Associated Projects | Transmission Owner | TSP Contact | Transmission Owner Project Number (Optional) | Projected In-Service Date (Month/Yr) | Service Level kV | Planning Charter Tier | Date Submitted TO ERCOT for RPG Review (Month/Yr) | Date RPG Review Completed (Month/Yr) | Date ERCOT BOD Review Completed (Month/Yr) | SSWG Base Case Related Bus Numbers (If applicable) (CSV) | Is the project reflected in SSWG Base Cases? (Y/N) | Phase Number | MOD Project Number
4274 | Navarro - Corsicana 69 kV Line | Upgrade existing line | Navarro | Corsicana |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R793 | 43600 | 69 | Tier 3 |  |  |  | 3468, 3475, 3479, 3480, 13468 | Y | 4648 | 4274
4825 | Crockett - Jewett 138kV Line | Upgrade existing line | Crockett | Jewett |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6061 | 43600 | 138 | Tier 3 |  |  |  | 3354, 3355, 3357, 3358, 3394 | Y | 5257 | 4825
5490 | Liggett - Hackberry 138 kV DCKT Line | Upgrade existing Liggett - Hackberry 138 KV Double Ckt Line | Liggett | Hackberry |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4222 | 43235 | 138 | Tier 3 |  |  |  | 1996, 1997, 2001, 2002, 2010, 11923, 15020, 15021, 2388, 15025, 15026, 15045, 15046 | Y | 6053 | 5490
4827 | Lufkin - Nacogdoches Southeast 138 kV Line | Upgrade existing line | Lufkin | Nacogdoches |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6062 | 45061 | 138 | Tier 3 |  |  |  | 3120, 3314, 3316, 3315, 3318 | Y | 5259 | 4827
5526 | Forney 345 kV Switching Station | Reconstruct existing 345 kV switching station | Forney |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4114 | 43600 | 345 | Tier 3 |  |  |  | 2467, 2433, 2437, 2478, 150189, 2438, 12438 | Y | 6078 | 5526
5436 | Morgan Creek - McDonald 138 kV Line | Upgrade existing line | Morgan Creek | McDonald Rd |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8360 | 45061 | 138 | Tier 3 |  |  |  | 1032, 1333 | Y | 5964 | 5436
5444 | Riverton-Solstice 345 kV Line | Establish new 345 kV line | Riverton | Solstice |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R8355 | 45471 | 345 | Tier 1 | 42480 |  |  | 11084, 60404 | Y | 5972 | 5444
5975 | Watermill - Camp Wisdom 138kV DCKT Line | Rebuild existing Watermill - Camp Wisdom 138 kV DCKT Line | Watermill Sw. Sta. | Camp Wisdom |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4216 | 43235 | 138 | Tier 3 |  |  |  | 2430, 2988, 2989, 2990, 3068 | Y | 6515 | 5975
6273 | Saginaw 345/138 kV autotransformer | Install new autotransformer and construct new 345 kV Line at Saginaw | SAGINAW | HICKS |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5274 | 43600 | 345 | Tier 2 |  |  |  | 11957, 11958, 1436, 2081, 1957 | Y | 6828 | 6273
17TPIT0024 | Payne - Anna Switch 138 kV Line | Upgrade existing line | Payne | Anna Switch |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R938-E | 43449 | 138 | Tier 3 |  |  |  | 1713, 1748, 1754, 1758, 2374 | Y | 3386 | 3213
6290 | Plano Tennyson 345/138 kV Sw. Sta. | Rebuild existing switching station | Plano Tennyson |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4237 | 44696 | 138 | Tier 3 |  |  |  | 12545, 2359, 2361, 2522, 2523 | Y | 6844 | 6290
4822 | Bell County (BEC) - Gabriel (LCRA) 138 kV | Upgrade existing line | Bell County | Gabriel |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2008 | 43966 | 138 | Tier 3 |  |  |  | 121, 132, 3640, 3688, 7346, 13640 | Y | 5253 | 4822
5627 | Hutto N- Gab, Hutto N - Hutto 138 kV Lines - Placeholder | Upgrade existing lines | Hutto North | Gabriel |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R2016 | 45061 | 138 | Tier 3 |  |  |  | 3664, 3666, 3667, 3668, 3669, 3677, 7346, 7528, 7532, 13666 | Y | 6182 | 5627
4834 | Cresson - Rocky Creek 138 kV Line | Construct new line | Cresson | Rocky Creek |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M5228 | 43966 | 138 | Tier 2 |  |  |  | 1881, 2204 | Y | 5261 | 4834
5467 | Nacogdoches Southeast_HertyN 345kV Line | Establish a new 345kV Line | Nacogdoches Southeast | Herty North |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6075 | 43966 | 345 | Tier 2 |  |  |  | 3119, 3321 | Y | 5996 | 5467
5475 | Lufkin Sw. Sta. - Herty North Sw. Sta. 345 kV Line | Construct a new 345 kV Line from Lufkin Sw. Sta. to Herty North Sw. Sta. | Lufkin Sw. Sta | Herty North Sw. Sta. |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6077 | 43966 | 345 | Tier 2 |  |  |  | 3117, 3321 | Y | 6005 | 5475
5524 | Royse South 345/138 kV Switching Station | Establish new 345/138 kV switching station | South Royse |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4234 | 43966 | 345 | Tier 3 |  |  |  | 2469, 2470, 12471, 2467, 2471, 2478, 2702, 2710, 3103, 12702 | Y | 6076 | 5524
6291 | Royse Sw. Sta. - Farmersville Sw. Sta. 345 kV DCKT Line | Rebuild existing 345 kV Line | Royse | Farmersville |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | M4255 | 45061 | 345 | Tier 3 |  |  |  | 1685, 2461, 2478 | Y | 6845 | 6291
5981 | Shamburger North 345/138 kV Sw. Sta. | Establish Shamburger North 345/138 kV Sw. Sta. | Shamburger North |  |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6083 | 43967 | 345 | Tier 3 |  |  |  | 3217, 3223, 3226, 2470, 3103, 3201, 3206 | Y | 6521 | 5981
16TPIT0054 | Dialville - Palestine South 138 kV Line | Upgrade existing Dialville - Palestine South line section | Dialville | Palestine South |  | ONCOR | Charles Saker charles.saker@oncor.com 214-743-6896 | R6019 | 43966 | 138 | Tier 3 |  |  |  | 3111, 3160, 3271, 3110, 3296 | Y | 3283 | 3114
5752 | City of Brady to Heartland: Build 69 kV line | Construct new 69 kV line from City of Brady to Heartland | City of Brady | Heartland | 796 - 0981 | AEP TNC | Michael Forcum mlforcum@aep.com 918-599-2674 | 3587 | 44712 | 69 | Tier 2 |  |  |  | 6383, 60386 | Y | 6317 | 5752

## Recently approved RPG project
Date Last Updated: | 2018-03-20 |  | Back | Back
Status | Final
Project Name | TDSP | Approve Date
IH20 SVC Project | TNMP | 2017-12-06
CenterPoint Energy-Freeport Master Plan Project | CNP | 2017-12-12
Pecos County Transmission Project, Option 1 | AEP | 2018-03-05
Far West Texas Project 2 | Oncor | 2018-05-22
Far West Texas Dynamic Reactive Devices Project | Oncor | 2018-05-22

## Model updates & corrections
Date Last Updated: | 2018-11-16 |  | Back
Status | Final
Model Corrections/Updates Made to the 2018 RTP Cases
Transmission Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2020 SUM | 2021 MIN | 2021 SUM | 2023 SUM | 2024 SUM
Added Far West Dynamic Reserve Devices at 1192 and 1193 | Oncor | X
Added Freeport Bridge-the-Gap projects | CNP | X | X | X | X | X | X
Added Freeport Master Plan projects | CNP |  |  |  | X | X | x
Updated ratings for Fox-Soda Springs 69kV line based on Brazos request | Brazos | X | X | X | X | X | X
Updated the status of the 138kV line at Killeen Park Street Tap based on Oncor request | Oncor | X | X | X | X | X | X
Updated the ratings of the brakers at Norwood station based on Oncor request | Oncor | X | X | X | X | X | X
Added Wirtz-Johnson City - Mountain Top Rebuild and Conversion to 138kV | PEC |  | X | X | X | X | X | Previous RTP project. Added to RTP Projects spreadsheet.
Updated the ratings for North Edinbug - McColl Road 138kV line | AEP |  | X | X | X | X | X
Updated emergency high limits for Cenizo, Del Sol, North Edinburg, and Rio Hondo 345kV buses | AEP |  | X | X | X | X | X
Updated the ratings for Charlotte to Dilley 69kV line | AEP |  |  | X | X | X | X | Previous RTP project. Added to RTP Projects spreadsheet.
Added BTU portion of Steele Store to Cooks Point 138kV line | LCRA |  |  |  |  | X | X
Opened Jacksonville Tap (3145) to Jacksonville North (3146) | Oncor | X | X | X | X | X | X | Oncor confirmed the line is normally open.
Opened branch from Nylon Tap (1055) to Nylon Switch (1056) | Oncor | X | X | X | X | X | X | Oncor confirmed the line is normally open.
Updated ratings for all 138kV lines around the Culberson Loop to 614/614/614 from 478/478/614 | Oncor |  | X | X | X | X | X | Oncor confirmed the updades
Added Far West Dynamic Reserve Device at 11190 | Oncor | X | [5 empty] | Oncor Confirmed
Added Far West Dynamic Reserve Devices at 11190 and 11189. Updated the 138kV topology in the Far West loop closer to the February SSWG cases. | Oncor |  | X | X | X | X | X | Oncor Confirmed
Corrected LEVEE_8 (111302) to LEVEE_GT1 (111301) line ratings | CNP |  |  | X |  |  |  | Based on TSP feedback.
345kV line from Moss (1018) to Odessa EHV (11028) should have ratings 1072 1072 1072 | Oncor | X | X | X | X | X | X | Oncor confirmed
Updated ratings for the 138 kV Circuits 1 and 2 from Dupont to Gregory Power to 279/330/470 and 404/470/470 | AEP |  | X | X | X | X | X | AEP confirmed
138kV line from Moss (1019) to Ector Harper (1292) should have ratings 214 214 214 | Oncor | X | X | X | X | X | X | Oncor confirmed
Updated ratings for the 345/138 kV autotransformer at Hutto (3696) to 700/750/750 MVA | Oncor |  |  |  |  | X |  | Added to 2023 NWNH sensitivity case. Oncor confirmed.
Open the 69kV line from Hoefs Road (6654) to Barrilla (6653) | AEP |  | X |  |  |  |  | Line is opened in the Higher Load Sensitivity Study year 2020 only. AEP confirmed.
Generation Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2020 SUM | 2021 MIN | 2021 SUM | 2023 SUM | 2024 SUM
Spencer Unit 4 (150071) & Unit 5 (150072) Online | Garland | X | [5 empty] | Spencer 4 and 5 will be operational starting June 1, 2018 as stated by their Notification of Change of Generation Resource Designation posted on MIS.
Added Reactive capability and changed voltage regulating target for Fluvanna Unit 1 (181951) and 2 (182001) | Oncor | X | X | X | X | X | X | Reactive capability information is from RARF
Set LEVEE GT1 (111301) generation to match its self-serve load | CNP | X | X | X | X | X | X | Based on TSP feedback.
Updated simple model topology for Grandview wind unit 3 (140653). There are no capacity changes. | Sharyland | X | X | X | X | X | X | Topology updated to reflect MOD modeling.
Load Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2020 SUM | 2021 MIN | 2021 SUM | 2023 SUM | 2024 SUM
Updated loads at Holford and Lookout | Garland | X | X |  | X | X | X | Updated loads based on Calvin's load review last year (NGRIP)
Opened LNG load at South Carbide | AEP |  |  | X | X | X | X | Updated based on TSP feedback.
Updated load at Vanderbilt 138 Sub (5585) | STEC | X | X | X | X | X | X | Updated based on TSP feedback.
Bus Voltage Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2020 SUM | 2021 MIN | 2021 SUM | 2023 SUM | 2024 SUM
Capacitor Bank Changes | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2020 SUM | 2021 MIN | 2021 SUM | 2023 SUM | 2024 SUM
Phase Shifters | TO | Case | [5 empty] | Comments
|  | 2019 SUM | 2020 SUM | 2021 MIN | 2021 SUM | 2023 SUM | 2024 SUM
8183 Thomaston | AEP | X | X | X | X | X | X | Control is normally on in normal operation
8255 Hamilton Road | AEP | X | X | X | X | X | X | Control is normally on in normal operation
8909 North Laredo Switch | AEP | X | X | X | X | X | X | Control is normally on in normal operation
85007 Nelson Sharpe | AEP | X | X | X | X | X | X | Control is normally on in normal operation

## Transmission & Gen Outages
Date Last Updated: | 2018-03-20 | Back
Status | Final
No transmission or generation outages with a duration longer than 6 months were available at the time of study

## CMP
Date Last Updated: | 2018-09-28 |  |  |  |  | Back
Status | Final
Constraint Management Plans Modeled in 2018 Regional Transmission Plan Studies
CMP Location and Description | TO | Reliability
|  | 2019 SUM | 2020 MIN | 2020 SUM | 2022 SUM | 2023 SUM
|  | N-1 | N-1 | N-1 | N-1 | N-1

## Gen add, ret. and mothball
Date Last Updated: | 2018-09-28 |  |  |  |  | Back
Status | Updated
Based on GIS report dated: | 2018-02-01
Based on NSO and Notice of Change of Generation Resource Designation received by | 4/13/2018
New generators that met PG 6.9 requirements
GINR Reference Number | Project Name | County | Projected Date | Fuel | MW For Grid | Changes From Last Report | Meets Section 6.9 Requirements (1)(b) through (1)(d) | 2019 | 2020 | 2021MIN | 2021 | 2022 | 2023 | 2024 | Comments
12INR0059b | HOVEY (Barilla Solar 1B) | Pecos | 2017-12-01 | Solar | 7 |  | Yes | X | X | X | X | X | X | X
14INR0031 | BTE (Baytown Chiller) | Chambers | 2018-01-01 | Gas | 270 |  | Yes | X | X | X | X | X | X | X
15INR0061 | LASSO | Brewster | 2018-01-01 | Solar | 50 |  | Yes | X | X | X | X | X | X | X
15INR0064 | NBOHR (BearKat Wind A) | Glasscock | 2018-01-01 | Wind | 197 | Projected Date | Yes | X | X | X | X | X | X | X
16INR0023 | LMESASLR (BNB Lamesa Solar 1) | Dawson | 2018-01-01 | Solar | 102 | Projected Date | Yes | X | X | X | X | X | X | X
13INR0049 | FEGC | Harris | 2018-02-01 | Gas | 129 | Projected Date | Yes | X | X | X | X | X | X | X
15INR0045 | RIGGINS | Pecos | 2018-02-01 | Solar | 150 |  | Yes | X | X | X | X | X | X | X
16INR0054 | NA | Harris | 2018-02-01 | Gas | 12 |  | Yes | X | X | X | X | X | X | X
17INR0022 | MIRAGE | Harris | 2018-02-01 | Gas | 11 |  | Yes | X | X | X | - | - | - | - | Generator will go offline after 2020
15INR0082 | FTWIND (Flat Top Wind I) | Comanche | 2018-03-01 | Wind | 200 |  | Yes | X | X | X | X | X | X | X
16INR0087 | RTS Wind Project | McCulloch | 2018-03-01 | Wind | 160 | Project Name | Yes | X | X | X | X | X | X | X
16INR0091 | HICKMAN | Reagan | 2018-04-01 | Wind | 300 | Projected Date | Yes | X | X | X | X | X | X | X
16INR0065 | CASL_GAP (Castle Gap Solar) | Upton | 2018-06-01 | Solar | 180 |  | Yes | X | X | X | X | X | X | X
16INR0086 | Cactus Flats Wind | Concho | 2018-06-01 | Wind | 148 | MW For Grid | Yes | X | X | X | X | X | X | X
18INR0013 | Denton Energy Center | Denton | 2018-07-01 | Gas | 226 |  | Yes | X | X | X | X | X | X | X
13INR0010a | Mariah Del Este | Parmer | 2018-09-01 | Wind | 152 |  | Yes | X | X | X | X | X | X | X
16INR0076 | Brazoria Energy G |  | 2018-10-01 | Gas | 90 |  | Yes | X | X | X | X | X | X | X
18INR0025 | Tahoka Wind | Lynn | 2018-10-01 | WIND | 505 | SFS | Yes | X | X | X | X | X | X | X
13INR0010c | Mariah Del Sur | Parmer | 2018-12-01 | Wind | 218 |  | Yes | X | X | X | X | X | X | X
14INR0023b | LHORN (Longhorn South W) | Briscoe | 2018-12-01 | Wind | 160 |  | Yes | X | X | X | X | X | X | X
14INR0030c | Panhandle Wind 3 | Carson | 2018-12-01 | Wind | 248 |  | Yes | X | X | X | X | X | X | X
14INR0038 | BAC | Galveston | 2018-12-01 | Gas | 390 | Projected Date | Yes | X | X | X | X | X | X | X
15INR0035 | Stella 1 Wind |  | 2018-12-01 | Wind | 201 |  | Yes | X | X | X | X | X | X | X
15INR0064b | BearKat Wind B | Glasscock | 2018-12-01 | Wind | 162 | Projected Date | Yes | X | X | X | X | X | X | X
16INR0023b | Lamesa Solar B (Phase II) | Dawson | 2018-12-01 | Solar | 50 | Projected Date, SFS | Yes | X | X | X | X | X | X | X
16INR0037c | Pumpkin Farm Wind | Floyd | 2018-12-01 | Wind | 281 |  | Yes | X | X | X | X | X | X | X
16INR0112 | Loma Pinta Wind | La Salle | 2018-12-01 | Wind | 200 | NEW | Yes | X | X | X | X | X | X | X
16INR0114 | Upton Solar | Upton | 2018-12-01 | Solar | 102 |  | Yes | X | X | X | X | X | X | X
16INR0115 | Waymark Solar | Pecos | 2018-12-01 | Solar | 182 |  | Yes | X | X | X | X | X | X | X
17INR0005 | Cabezon Wind | Starr | 2018-12-01 | Wind | 238 | Project Name, SFS | Yes | X | X | X | X | X | X | X
17INR0020a | RE Maplewood 2a Solar | Pecos | 2018-12-01 | Solar | 100 |  | Yes | X | X | X | X | X | X | X
15INR0059 | Emerald Grove Solar | Pecos | 2019-01-01 | Solar | 108 | Project Name | Yes | X | X | X | X | X | X | X
11INR0054 | Midway Wind | San Patricio | 2019-03-01 | Wind | 163 |  | Yes | X | X | X | X | X | X | X
11INR0062 | Patriot Wind | Nueces | 2019-04-01 | Wind | 180 | Projected Date | Yes | X | X | X | X | X | X | X
17INR0027b | Coyote Wind | Scurry | 2019-05-01 | Wind | 242 |  | Yes | X | X | X | X | X | X | X
16INR0003 | LEVEE (Freeport LNG) | Brazoria | 2019-06-01 | Gas | 11 |  | Yes | X | X | X | X | X | X | X
16INR0062b | Lockett Wind | Wilbarger | 2019-06-01 | Wind | 184 |  | Yes | X | X | X | X | X | X | X
18INR0043 | Edmondson Ranch Wind | Glasscock | 2019-09-01 | Wind | 292 | SFS | Yes | X | X | X | X | X | X | X
13INR0038 | Wildrose Wind | Swisher | 2019-10-01 | Wind | 212 |  | Yes | - | X | X | X | X | X | X
12INR0060 | Infinity Live Oak Wind | Schleicher | 2019-12-01 | Wind | 200 |  | Yes | - | X | X | X | X | X | X
13INR0005c | Grandview W 3 | Carson | 2019-12-01 | Wind | 188 |  | Yes | - | X | X | X | X | X | X
14INR0044 | West of Pecos Solar | Reeves | 2019-12-01 | Solar | 100 | Projected Date | Yes | - | X | X | X | X | X | X
14INR0045a | Torrecillas Wind A | Webb | 2019-12-01 | Wind | 200 |  | Yes | - | X | X | X | X | X | X
14INR0045b | Torrecillas Wind B | Webb | 2019-12-01 | Wind | 200 |  | Yes | - | X | X | X | X | X | X
17INR0020b | RE Maplewood 2b Solar | Pecos | 2019-12-01 | Solar | 100 |  | Yes | - | X | X | X | X | X | X
17INR0020c | RE Maplewood 2c Solar | Pecos | 2019-12-01 | Solar | 100 |  | Yes | - | X | X | X | X | X | X
17INR0020d | RE Maplewood 2d Solar | Pecos | 2020-12-01 | Solar | 100 |  | Yes | - | - | X | X | X | X | X
17INR0020e | RE Maplewood 2e Solar | Pecos | 2020-12-01 | Solar | 100 |  | Yes | - | - | X | X | X | X | X
Retired units
Unit Name | MW For Grid | 2019 | 2020 | 2021MIN | 2021 | 2022 | 2023 | 2024 | Comments
PEARSALL (PEARSALL_PEARS_1, PEARSALL_PEARS_2, PEARSALL_PEARS_3) | 61 | X | X | X | X | X | X | X | Per Dec 2017 CDR: Since 8/1/2017
GREENS BAYOU STG U5 (GBY_GBY_5) | 371 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 12/31/2017
S R BERTRON (SRB_SRBGT_2, SRB_SRB_G3, SRB_SRB_G4) | 420 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 12/31/2017
S R BERTRON U1 & U2 (SRB_SRB_G1, SRB_SRB_G2) | 292 | X | X | X | X | X | X | X | Per Dec 2017 CDR: Since 5/15/2013
MONTICELLO (MNSES_UNIT1, MNSES_UNIT2, MNSES_UNIT3) | 1865 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 1/4/2018
SANDOW (SDSES_UNIT4, SD5SES_UNIT5) | 1200 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 1/11/2018
BIG BROWN (BBSES_UNIT1, BBSES_UNIT2) | 1208 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 2/12/2018
Mothballed units
Unit Name | MW For Grid | 2019 | 2020 | 2021MIN | 2021 | 2022 | 2023 | 2024 | Comments
B M DAVIS STG U1 (B_DAVIS_B_DAVIG1) | 330 | X | X | X | X | X | X | X | Per Dec 2017 CDR: On 12/31/2017
SPENCER (STG U4, STG U5) | 118 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 1/3/2018
GIBBONS CREEK U1 (GIBCRK_GIB_CRG1) | 470 | [7 empty] | Per Dec 2017 CDR: Return to service between May-June 2018
J T DEELY U1 & U2 | 840 | X | X | X | X | X | X | X | Per Dec 2017 CDR: As of 12/31/2018

## Renewable Generation Dispatch
Date Last Updated: | 2018-03-20 | Back
Status | Final
Solar
Information obtained from the spreadsheet "CDR Summer PeakAveSolarCapacityPercentages 11-20-2017" posted on the ERCOT website under Resource Adequacy.
* SOLARPEAKPCT Values | 75%
* The methodology for calculating SOLARPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See: http://www.ercot.com/content/wcm/current_guides/53528/03_030116_Nodal.doc
Wind
Information obtained from the spreadsheet "CDR Summer PeakAveWindCapacityPercentages 11-20-2017" posted on the ERCOT website under Resource Adequacy.
Outside Study Region
WINDPEAKPCT Values *
Summer, Non-Coastal | Summer, Coastal
14% | 59%
* The methodology for calculating WINDPEAKPCT values is outlined in ERCOT Protocol Section 3.2.6.2.2. See: http://www.ercot.com/content/wcm/current_guides/53528/03-110117_Nodal.doc
Inside Study Region
Average Capacity Factor (15th Percentile)
WZ_FAR_WEST | 4.36%
WZ_NORTH | 5.57%
WZ_NORTH_CENTRAL | 0.74%
WZ_SOUTH_CENTRAL | 1.1%
WZ_SOUTHERN | 18.67%
WZ_WEST | 2.33%
Hydro
Unit specific generation MW dispatch modeled based on historical dispatch levels during the top 20 load hours of the last three years.
AMI_AMISTAG1 (H1) | 18.65
AMI_AMISTAG2 (H2) | 28.7
AUS_AUSTING1 (H1) | 8
AUS_AUSTING1 (H2) | 8.5017
BUC_BUCHANG1 (H1) | 16
BUC_BUCHANG2 (H2) | 16
BUC_BUCHANG3 (H3) | 17
CAN_CANYHYG1 (H1) | 0
CAN_CANYHYG1 (H2) | 0
DND_DENISOG1 (H1) | 40
DND_DENISOG2 (H2) | 40
EA_EAGLE_HY1 (H1) | 0
EA_EAGLE_HY1 (H2) | 0
EA_EAGLE_HY1 (H3) | 0
FAL_FALCONG1 (H1) | 7.55
FAL_FALCONG2 (H2) | 8.3187
FAL_FALCONG3 (H3) | 8.65
INKS_INKS_G1 (H1) | 13.37
MAR_MARBFAG1 (H1) | 19.7455
MAR_MARBFAG2 (H2) | 19.3043
MAR_MARSFOG1 (H1) | 35.5667
MAR_MARSFOG2 (H2) | 35.8158
MAR_MARSFOG3 (H3) | 28.7556
WIR_WIRTZ_G1 (H1) | 28.78
WIR_WIRTZ_G2 (H2) | 29
WND_WHITNEY1 (H1) | 19.8967
WND_WHITNEY2 (H2) | 13.0217
Wind (Min Case)
Non-Coastal | Coastal
52.33% | 25.09%

## Switchable Generation
Date Last Updated: | Tuesday, March 20, 2018 |  |  |  |  | Back
Status | Updated
Operational Resources (Switchable)
UNIT NAME | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027
ANTELOPE IC 1 | ANTLP_G1 | HALE | GAS | WEST | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ANTELOPE IC 2 | ANTLP_G2 | HALE | GAS | WEST | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ANTELOPE IC 3 | ANTLP_G3 | HALE | GAS | WEST | 2016 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
ELK STATION CTG 1 | AEEC_ELK_1 | HALE | GAS | WEST | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
ELK STATION CTG 2 | AEEC_ELK_2 | HALE | GAS | WEST | 2016 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
TENASKA FRONTIER STATION CTG 1 | FTR_FTR_G1 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | - | - | - | - | - | - | -
TENASKA FRONTIER STATION CTG 2 | FTR_FTR_G2 | GRIMES | GAS | NORTH | 2000 | 160 | 160 | 160 | - | - | - | - | - | - | -
Switchable Capacity Unavailable to ERCOT | SWITCH_UNAVAIL |  | GAS |  |  | -843.8 | -843.8 | -843.8 | -523.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8 | -543.8
*Note: the Tensaka Frontier is going to keep 300 MW switched out but it won’t be necessarily from particular units.

## DC Tie modeling & dispatch
Date Last Updated: | 2018-03-20 |  | Back
Status | Final
Reliability Analysis
DC Tie dispatch - Summer peak conditions (MW)
DC_E | 600 | Import
DC_N | 220 | Import
DC_L* | 100 | Export
DC_R* | 300 | Export
DC_S* | 30 | Export
* In the events that thermal overloads are resolved by curtialing the DC Tie exports, the events and the curtailed amounts will be documented.
Economic Analysis
DC Tie dispatch - 8760-hour assumptions
DC_E | Import only | Modeled as a pseudo-generator with characteristics developed based on historical operational data
DC_N | Import + export | Modeled as a pseudo-generator and a demand profile with characteristics developed based on historical operational data.
DC_L* | Export only | Demand profile developed based on the historical operational data
DC_R* | Export only
DC_S* | Export only

## Reserve Requirement
Date Last Updated: | 2018-03-20 | Back
Status | Final
Reliabity Cases | 2800 MW
The reserve requirements used in the reliability models account for the outage of ERCOT's two largest units as well as the increased losses observed during such an G-1 & N-1 outage.
Economic Analysis | 1622 MW
The reserve requirements used in the economic models are based on a review of ERCOT’s 2018 Responsive Reserve and Regulation Up requirements. Note that the value is less than 2800 MW since the MW contribution of load resources is not an input into the economic model.

## Fuel Price Assumptions
Date Last Updated: | 2018-03-14 |  |  |  |  | Back
Status | Final
Source | EIA 2018 AEO High Oil and Gas Resource and Technology Case
Natural Gas Price Forecast ($/MMBtu)
Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Average
2018 | 3.08 | 3.05 | 3.01 | 2.86 | 2.87 | 2.88 | 2.9 | 2.92 | 2.92 | 2.94 | 3.02 | 3.14 | 2.9658
2019 | 3.37 | 3.35 | 3.3 | 3.15 | 3.15 | 3.15 | 3.18 | 3.2 | 3.2 | 3.22 | 3.31 | 3.44 | 3.2517
2020 | 3.68 | 3.66 | 3.6 | 3.43 | 3.44 | 3.45 | 3.47 | 3.51 | 3.51 | 3.52 | 3.61 | 3.75 | 3.5525
2021 | 3.48 | 3.46 | 3.41 | 3.25 | 3.26 | 3.27 | 3.29 | 3.32 | 3.32 | 3.33 | 3.42 | 3.55 | 3.3633
2022 | 3.38 | 3.35 | 3.3 | 3.14 | 3.15 | 3.16 | 3.19 | 3.21 | 3.21 | 3.23 | 3.31 | 3.44 | 3.2558
2023 | 3.44 | 3.41 | 3.37 | 3.21 | 3.22 | 3.23 | 3.24 | 3.27 | 3.27 | 3.29 | 3.38 | 3.51 | 3.32
2024 | 3.58 | 3.55 | 3.5 | 3.34 | 3.35 | 3.35 | 3.38 | 3.4 | 3.4 | 3.42 | 3.51 | 3.65 | 3.4525

## Reliability case-Load Forecast
Date Last Updated | 2018-09-28 |  |  |  |  | Back
Status | Final
SSWG Load in 17SSWG dated 10/12/2017 less Self-Served (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | NCP Total
2020 | 23601.02 | 3014.97 | 5119.25 | 1706.41 | 26000.65 | 13699.2 | 6533.2 | 2304.42 | 81979.12
2021 | 23627.81 | 3024.46 | 5337.64 | 1714.02 | 26500.87 | 13939.8 | 6731.41 | 2324.35 | 83200.36
2023 | 23913.62 | 3093.33 | 5764.83 | 1723.04 | 27127.34 | 14385.36 | 6928.02 | 2363.26 | 85298.8
2024 | 24064.53 | 3116.63 | 5890.18 | 1735.55 | 27423.1 | 14606.03 | 7023.84 | 2379.05 | 86238.91
ERCOT 90th Percentile Load forecast for RTP (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | NCP Total
2020 | 22102.5013 | 2789.4063 | 3840.1405 | 1463.9426 | 26621.7731 | 13142.9464 | 6175.4019 | 1978.3188 | 78114.4309
2021 | 22418.5275 | 2808.5689 | 4139.2481 | 1467.1587 | 26887.6166 | 13269.3149 | 6317.4905 | 2005.5313 | 79313.4565
2023 | 23159.5318 | 2853.2676 | 4801.672 | 1475.1755 | 27489.642 | 13564.336 | 6648.6934 | 2063.5414 | 82055.8597
2024 | 23482.376 | 2871.2928 | 5099.8361 | 1478.1852 | 27746.2601 | 13695.1354 | 6790.9017 | 2090.9087 | 83254.8961
2018 RTP final load forecast based on on 5% boundary threshold (MW)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | Total
2020 | 27180 | 2950 | 4557 | 1503 | 26541 | 13666 | 6938 | 2248 | 85583
2021 | 27513 | 2971 | 4837 | 1507 | 26781 | 13904 | 6871 | 2272 | 86656
2023 | 27918 | 3018 | 5403 | 1515 | 27321 | 14217 | 7217 | 2321 | 88930
2024 | 28070 | 3037 | 5543 | 1518 | 27568 | 14355 | 7365 | 2343 | 89799
2018 RTP final load forecast for Off-Peak Case (MW) (based on 2021 SSWG Min Case)
Year | Coast | East | Far West | North | North Central | South Central | Southern | West | Total
2021 | 13381 | 1075 | 2448 | 795 | 9167 | 4652 | 2694 | 1014 | 35226

## Sensitivity Analysis
Date Last Updated: | 2018-11-13 |  |  |  |  | Back
Status | Final
Sensitivity 1: | No-Wind-No-Hydro Sensitivity for Summer Peak Conditions
Year | Wind Capacity Unavailable in the sensititivy cases |  |  |  | Hydro Capacity Unavailable in the sensititivy cases
| EC | NNC | WFW | SSC | EC | NNC | WFW | SSC
2020 | - | 432 | 318 | 1030 | - | 113 | 96 | 251
2023 | - | 443 | 318 | 1030 | - | 113 | 96 | 251
Sensitivity 2: | Wind Capacity Unavailable in the sensititivy cases EC: High-Wind-Low-Load Sensitivity for Off-Peak Conditions
Case | Wind Capacity Unavailable in the sensititivy cases EC: ERCOT Load (MW); Wind Capacity Unavailable in the sensititivy cases NNC: DC Tie Export* (MW); Wind Capacity Unavailable in the sensititivy cases WFW: Wind Output (MW)
|  |  | South-Coastal | West-North | Panhandle | Total
2021 Min | 35226 | -200 | 1832 | 5495 | 2846 | 10173
2021 HWLL | 37066 | 1250 | 4291 | 12088 | 3868 | 20247
Sensitivity 3: | Wind Capacity Unavailable in the sensititivy cases EC: Higher WFW Load
Year | Wind Capacity Unavailable in the sensititivy cases EC: Far West Weather Zone Load; Wind Capacity Unavailable in the sensititivy cases NNC: West Weather Zone Load
2020 | Wind Capacity Unavailable in the sensititivy cases EC: 5128; Wind Capacity Unavailable in the sensititivy cases NNC: 2357
2023 | Wind Capacity Unavailable in the sensititivy cases EC: 5957; Wind Capacity Unavailable in the sensititivy cases NNC: 2426