## Slide 1
PGRR122
PLWG
December 18, 2024
Jeff Billo
ERCOT Operations Planning

## Slide 2: PGRR122 Background
Southern Cross Directive 9 Study showed that the loss of 1,488 MW of demand during certain system conditions could cause frequency to exceed 60.6 Hz, which could lead to generator tripping and frequency instability
  NPRR1034 approved to limit DC tie exports (and imports) for frequency stability
https://www.ercot.com/files/docs/2021/07/07/AS_Impact_and_Overshoot_Study_Report_v14_Final.docx
Scenario Name | Inertia (GW·s) | Load (GW) | Wind (GW) | Synchronous Gen (GW)
Scenario 0 | 130 | 34 | 15.5 | 19
Scenario 1 | 130 | 34 | 10 | 24.5
Scenario 2 | 130 | 32 | 5 | 27.5
Scenario 3 | 130 | 32 | 3.5 | 29
Scenario 4 | 120 | 29.9 | 3.5 | 26.9
Scenario 5 | 110 | 27.2 | 3.5 | 24.2
 | Scenario 0 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5
Highest Frequency Overshoot (Hz) DR=2.0 | 60.38 | 60.47 | 60.51 | 60.53 | 60.60 | 60.70
Highest Frequency Overshoot (Hz) DR=0.0 | 60.42 | 60.54 | 60.60 | 60.62 | 60.73 | 60.89

## Slide 3: PGRR122
Problem Statement:
  Several Large Load interconnection (LLI) requests that exceed 1,000 MW and multiple areas with smaller LLI that in aggregate exceed 1,000 MW
  ERCOT has observed poor voltage ride through capability of Large Loads: https://www.ercot.com/files/docs/2024/11/18/ERCOT%20Large%20Load%20Events_PDCWG_19Nov2024.pdf
  Southern Cross study showed that there is a frequency stability limit for the amount of demand that can be lost under contingency
  Large Loads do not register as an ERCOT Market Participant, so ERCOT cannot curtail them in real-time (like a DC tie)
Proposed Solution:
  Establish a maximum amount of load (MW) that can be lost under contingency to maintain frequency stability
    Conduct a study to determine maximum loss of load limit
    Based on the Southern Cross study limit of 1,488 MW, and considering a margin to account for system changes, set the limit to be 1,000 MW initially

## Slide 4: Next Steps
DWG Feedback
PLWG Feedback

## Slide 5
Questions?