## Slide 1
IRR Primary Frequency Response when Curtailed
ERCOT Staff
IBRWG
1/17/2025

## Slide 2: Agenda
ERCOT PFR expectation
IBRWG/OEM discussions
What ERCOT is seeing from IRRs
Potential approach to deal with the concerns

## Slide 3: Grid Code : Primary Frequency Response Requirement
All online resources are required to assist in ERCOT’s frequency control and provide a “governor-like” response to frequency deviations when they have headroom/legroom.
ERCOT is noticing that several IRRs when curtailed to low ouput(including down to zero) are failing BAL-TRE-001 evaluation. We have been talking with the OEMs to understand the capabilities and limitations of various technologies providing PFR when curtailed.
OEMs brought this issue to the IBRWG for further discussion and potential resolution.
Generator Type | Max. Droop % Setting
Combustion Turbine (Combined Cycle) | 4%
All Other Generating Units/Generating Facilities/ESRs/Controllable Load Resources | 5%

## Slide 4: What we heard in IBRWG meetings
With IBRWG help, ERCOT got following feedback from OEMs
At the Sep 16, 2024 IBRWG meeting, Vestas presented that their Wind Turbine’s will disconnect or enter pause mode when curtailed below controllable active power range including when curtailed to 0 MW. Vestas further proposed potential solutions for the limitations and capabilities that may be “Vestas-specific”: 1) Creating BAL-001-TRE-2 exclusion for response limitation, 2)Introducing a non-zero LSL and 3)Separate HSL for dispatching vs PFR.
At the Oct 11 2024 IBRWG meeting, SMA and other anonymous solar OEM presented that their inverters does not have any limitations in providing PFR during deep curtailments.
At the Nov 15, 2024 IBRWG meeting,
  Nordex presented that their Wind Turbine’s will disconnect when curtailed below Technical Minimum(TM) (10% of rated power) or curtailed to 0 MW. Nordex proposed potential solution to introduce a TM for frequency control, excluding PFR contribution below this minimum operating limit.
  Industry expert from HickoryLedge presented that the active power control at low power levels, whether due to deep curtailments or low wind speed is extremely challenging and subject to multiple physical and stability constraints.

## Slide 5: What we are seeing from IRRs
Notes: 11/23/24 18:18

## Slide 6: What we are seeing from IRRs
Notes: 11/23/24 18:18

## Slide 7: What we are seeing from IRRs
Notes: 11/23/24 18:18

## Slide 8: What we are seeing from IRRs
Notes: 3/17/2024 15:16

## Slide 9: What we are seeing from IRRs
Notes: 3/17/2024 15:16

## Slide 10: ERCOT’s thoughts on potential approach for this issue
To maintain ERCOT system reliability, ERCOT may have to curtail the IRR units down to 0 MW and a non-zero LSL for the IRRs may hamper the curtailment.
The parameters that limit the capability to provide PFR when curtailed seems to vary based on the OEM, real-time operating conditions, state of the equipment, etc. Furthermore, there was no feedback from several other OEMs on their limitations during these discussions.
Recognizing that during real-time there can be operating conditions during which some wind resources may not be able to provide PFR, A change that can be implemented relatively quickly without impacting ERCOT’s reliability is to add this as an additional exclusion to the BAL-001-TRE-2 PFR exclusion process. Doing so will allow ERCOT to assess the extent of this issue.
ERCOT may propose additional solutions in the future as we gain more knowledge on the limitations and capabilities of the IRRs during curtailment.
ERCOT is seeking IBRWG’s inputs on this approach.

## Slide 11
DISCUSSION