## Slide 1
Strategic Energy & Risk Valuation Model (SERVM) Projects for 2025
Pete Warnken
Resource Adequacy
Supply Analysis Working Group
January 24, 2025

## Slide 2: 2025 SERVM Projects List
  Weather Event Modeling Enhancements
    January Reliability Risk Analysis
    Event Duration Risk Assessment
  Zonal Reliability Model Analysis & Development
  Reliability Standard Assessment Prototyping
  Supply Deliverability Analysis for Transmission Planning
  ELCC Methodology Refinement
  Probabilistic Assessment (for NERC LTRA)

## Slide 3: Weather Event Modeling Enhancement: January Analysis
  The historical weather year approach used in SERVM is dependent on the timing of extreme weather events. The two most extreme winter events in the historical simulated window were in December 1989 and February 2021. The timing of these events are coincidental, and so the distribution of potential extreme peak loads for January is under-represented.
  The purpose of this analysis is to shift load/wind/solar profiles, as statistically justified, such that the distribution of the most extreme peaks and associated generator outages covers the full range of winter dates with potential risk.
    This approach keeps the winter season loss-of-load risk the same, but the risk distribution is modified to better reflect the risk in January.

## Slide 4: Weather Event Modeling Enhancement: Duration Analysis
  Current SERVM inputs are calibrated to system average conditions which may understate the risk of extended outages driven by long individual generator outages.
  PowerGEM will explore assumptions around cold weather outage durations by calibrating to discrete unit-level outage events during cold weather.
  The effects of fuel supply outages and repair times will also be evaluated, and more granular cold weather outage inputs will be defined in SERVM.
  The results of the base case assumptions will be compared to the adjusted inputs to determine if and how the modified outage duration approach is applied going forward.

## Slide 5: Zonal Reliability Model Analysis & Development
  Purpose of this project is to transform the current SERVM implementation from a single-zone model to a multi-zonal model to account for inter-zonal generation deliverability impacts on system reliability.
    Develop zone definitions using TARA* clustering functionality that considers electrical distances of each bus point with respect to every defined flowgate (Generic Transmission Constraint (GTC) or other constraint).
    Determine transfer capabilities between the zones, imports/exports limits for neighboring grids, and aggregated transfer capabilities as applicable.
    Using the zone definitions, develop synthetic zonal load profiles for 44 weather years and allocate resources to the zones.
    Conduct simulations for one study year (2026) to assess generation deliverability impacts in relation to the original single-zone model.
*TARA = PowerGem’s “Transmission Adequacy & Reliability Assessment” tool

## Slide 6: Reliability Standard Assessment Prototyping
  The prototyping project will explore how the Reliability Assessment study will be performed starting in 2026
    PowerGEM will work with ERCOT and stakeholders to understand key design considerations for analyzing and ensuring reliability.
    Given the nascent proposed approach to analyzing transmission and generation reliability using the zonal SERVM implementation, formal procedures will be evaluated and established to ensure the results from this process are appropriately built into the Reliability Standard’s Reliability Assessments going forward.
    A test implementation (trial simulation for forecast year 2026) will be performed to provide guidance on potential outcomes and necessary refinements for the first official Reliability Assessment starting in 2026.

## Slide 7: Supply Deliverability Analysis for Transmission Planning
  This is an exploratory project intended to investigate how the probabilistic multi-zonal SERVM implementation can be integrated into ERCOT’s transmission planning processes to support generation deliverability risk considerations.
    Task 1: Data Collection, Base Case Setup, and Input Validation.
    Task 2: Base network development using SERVM and TARA, plus a change case with one transmission system upgrade.
    Task 3: Simulate up to 1,000 load flow cases comprised of a combination of load, wind, and solar conditions plus generator/transmission component contingencies.
    Task 4: PowerGEM will aggregate reliability results for the full distribution of scenarios (load flow cases).
    Task 5: PowerGem will conduct benefits analysis “test cases” for several objectives in FERC Order 1920, such reducing Loss of Load Probability (LOLP)/reserve margin and mitigating extreme weather impacts.

## Slide 8: Effective Load Carrying Capability (ELCC) Methodology Refinement
This project is intended to investigate potential refinements to the ELCC approach developed for CDR reporting.
  Explore refinements to seasonal and risk period ELCC estimation.
  Consider expanding portfolio resource penetration levels.
  Investigate incorporating load shape changes due to planned. interconnection of Large Loads (data centers, industrial, and crypto-currency mining, etc.).
  Investigate refining the SERVM results calibration approach that uses Excel.
  If the project budget allows, continue investigating estimation of thermal ELCCs. (The 2022 ELCC study provides indicative thermal ELCCs: https://www.ercot.com/files/docs/2022/12/09/2022-ERCOT-ELCC-Study-Final-Report-12-9-2022.pdf.)

## Slide 9: NERC Probabilistic Assessment
  NERC now requires annual probabilistic reliability assessments be conducted every year, rather than every other year, based on the resources and load forecast used for the NERC Long Term Reliability Assessment.
  This project entails PowerGem supporting ERCOT staff in conducting the Probabilistic Assessment using SERVM.
    The assessment calls for probabilistic simulations for two forecast years (assumed to be 2027 and 2029 for this year’s assessment).
    Preliminary and final results are typically due in mid-August and mid-September, respectively.