## Slide 1
PDCWG Report to ROS
Chair: Kevin Bunch, EDF Trading North America
Vice Chair: Chad Mulholland, NRG
ROS
February 6th, 2024

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    PDCWG Leadership Volunteers
    ERCOT Frequency Control Metrics and Regulation Reports
    TRE Report
    Analysis of Disturbances
  BAL-001-TRE-2 FMEs and IMFR
    0 FME in the month of December
    Note that occurrence of FMEs is down a lot – 2021 had 19; 2022 had 16; 2023 had 7; 2024 had 6
  Frequency Control Report

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 395 MW/0.1 Hz
IMFR Performance currently
1552.00 MW/0.1HZ

## Slide 5
Questions?

## Slide 6: Frequency Control Report
October 2024

## Slide 7: CPS1 Performance

## Slide 8: RMS1 Performance of ERCOT Frequency
Notes: 13.95 mHz on avg for December 2024

## Slide 9: Frequency Profile Analysis

## Slide 10: Time Error Corrections

## Slide 11: ERCOT Total Energy
Notes: 35,297,482 MWh

## Slide 12: ERCOT Total Energy from Wind Generation
Notes:   9,236,413 MWH

## Slide 13: ERCOT % Energy from Wind Generation
Notes: 26.17% of total energy was provided by wind generation

## Slide 14: ERCOT Total Energy from Solar Generation
Notes: 3,002,040 MWh

## Slide 15: ERCOT % Energy from Solar Generation
Notes: 8.50% of total energy was provided by solar generation

## Slide 16: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in December 2024 = 162,482 MW*s on December 30th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
December Data:
Mean: 199,978 MW*s
Max: 264,996 MW*s on December 6th
Min: 162,482 MW*s on December 30th

## Slide 17: ERCOT Inertia Trend
Notes: Summary of ERCOT inertia for the previous 10 years. Lowest inertia this year was on March 29th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.