## Slide 1
Review of Requirements and Deadlines
Andrew Gallo
ERCOT Legal Department
NOGRR245 Workshop
February 10, 2025

## Slide 2: NOGRR245 Essentials
  On 8/20/24, BOD approved
  On 9/26/24, Commission approved NOGRR245 effective 10/1/24
  Based on representations by Market Participants during NOGRR245 drafting, it was understood Resource Entities would maximize FRT and VRT capabilities to fullest extent equipment allows
    Resources not to merely meet minimum ride-through requirements
  Thus, revised NOG require all IBRs, Type 1 WGRs and Type 2 WGRs to maximize – to the fullest extent possible – FRT and VRT capability
    “Maximize” means software, settings, firmware, and parameterization changes (including memory upgrades) to maximize ride-through capabilities
  Most of discussion addresses requirements assuming protection systems, controls and other plant equipment are maximized to fullest extent possible
Disclaimer: These slides attempt to summarize requirements/dates but actual language of NOG takes precedence over the slides

## Slide 3: NOGRR245 Essentials
  Frequency Ride-Through (FRT)
  Resources must ensure FRT capability is set to maximum level equipment allows to meet or exceed § 2.6.2.1(1) - (5) ASAP but no later than 12/31/25 (or synchronization if synchronizing after 12/31/25) [§ 2.6.2.1(6)]
Resource w/ SGIA, before 8/1/24 that cannot meet § 2.6.2.1(1) – (6) by 12/31/25 must – by 4/1/25 - submit IFRTCR (§ 2.11.1) and request extension and comply with FRT requirements in effect on 5/1/24 until it maximizes FRT capability [§2.6.2.1(7)]
  If it cannot meet § 2.6.2.1(1) – (6) even with extension, must – by 4/1/25 - submit IFRTCR (§ 2.11.1) and request exemption and meet §2.6.2.1.1 [§2.6.2.1(7)]
  While performing maximization activities, must comply with FRT requirements in effect on 5/1/24 [§ 2.6.2.1(7)]

## Slide 4: NOGRR245 Essentials
  Voltage Ride-Through (VRT)
  Every IBR, Type 1 WGR and Type 2 WGR must maximize performance of protection systems, controls, and other plant equipment to meet and, if possible, exceed IEEE 2800-2022 Sections 5, 7 and 9 [§ 2.9.1(8); § 2.13(1)]
    Resource w/ SGIA before 8/1/24 that cannot fully meet IEEE 2800-2022, must maximize protection systems, controls, and other plant equipment to achieve, as close as reasonably possible, IEEE 2800-2022 ASAP but no later than 12/31/25 or COD (whichever is later) [§ 2.9.1(8)]
  Resource with SGIA before 8/1/24 must at least meet VRT requirements in §2.9.1.2(1)-(8) ASAP but no later than 12/31/25 or COD (whichever is later) [§2.9.1.2(8)]
    If cannot meet § 2.9.1.2(1)-(7) by 12/31/25 after maximizing protection systems, controls and other plant equipment, it must - by 4/1/25 - submit IVRTCR (§ 2.11.2) and request extension and comply with VRT requirements in effect on 5/1/24 until it maximizes FRT capability [§ 2.9.1.2(9)]
    If it cannot meet § 2.9.1.2(1)-(7) even with extension, must - by 4/1/25 - request an exemption and comply with VRT requirements in effect 5/1/24 until it maximizes VRT capability [§ 2.9.1.2(9)]

## Slide 5: NOGRR245 – Review of Requirements & Dates
Requirement | Deadline
All IBRs/Type 1/Type 2 WGRs must maximize FRT capability to maximum level equipment allows and meet FRT requirements in §2.6.2.1(1)-(5) Upon completing maximization work, inform ERCOT [§ 2.11(3)] | ASAP but no later than 12/31/25 (or synch if after 12/31/25) [§2.6.2.1(6)]
Resource w/ SGIA before 8/1/24 that cannot meet § 2.6.2.1(1)-(5) must meet FRT requirements in §2.6.2.1.1(2), (3) | ASAP [§2.6.2.1.1(1)]
Resource that cannot remain reliably connected to grid per §2.6.2.1.1(2), must provide info required in §2.11 | ASAP [§2.6.2.1.1(3)]

## Slide 6: Frequency Ride-Through

## Slide 7: NOGRR245 – Review of Requirements & Dates
Requirement | Deadline
All Resources must maximize to the fullest extent possible protection systems, controls, & other equipment to meet/exceed VRT requirements in IEEE 2800-2022, Sections 5, 7 and 9 | Later of 12/31/25 or COD [§2.9.1(8)]
Resource w/ SGIA after 8/1/24 (or existing w/ GIM) must meet IEEE 2800-2022 If cannot do so by synch date, request temp extension | 12/31/25 or sync date Request extension by 4/1/25 and comply upon sync [§2.9.1(2), (3), (6)]
Resource w/ SGIA after 8/1/24 (or existing w/ GIM) that cannot meet IEEE 2800-2022 after maximizing must meet §2.9.1.1(1)-(7) If cannot do so, request temp extension | 12/31/25 Request extension by 4/1/25 [§2.9.1(1)(a); §2.9.1.1(8)]
IBR with SGIA after 8/1/24 seeking extension to meet requirements in §2.9.1.1(1) Table A must submit info in §2.12.1.2(5)(a), (b) and (c) | 4/1/2025 [§2.12.1.2(5)]
Type 3 WGR may seek extension for modifications to meet §2.9.1.1(1) Table A During extension, must set VRT capability to maximum level equipment allows ASAP | 4/1/25 [§2.9.1.1(9)]

## Slide 8: NOGRR245 Review of Requirements & Dates
Requirement | Deadline
Resource w/ SGIA before 8/1/24 and cannot meet IEEE 2800-2022 must maximize to achieve, as close as reasonably possible, IEEE 2800-2022 | ASAP (no later than 12/31/25 or COD, whichever is later) [§2.9.1.2(8)]
Resource w/ SGIA before 8/1/24 - after maximizing to achieve as close as possible IEEE 2800-2022 - must maximize to meet and, if possible, exceed in §2.9.1.2(1) - (7) | ASAP (no later than the later of 12/31/25 or COD) [§2.9.1(1)(b); §2.9.1.2(8)]
Resource w/ SGIA before 8/1/24 that cannot meet 2.9.1.2(1)-(7) by 12/31/25 must submit IVRTCR and request extension and comply w/ VRT requirements in effect on 5/1/24 | 4/1/25 [§2.9.1.2(9)]
Resource w/ SGIA before 8/1/24 that cannot meet §2.9.1.2(1)-(7) even w/ extension must submit IVRTCR and request exemption and comply w/ VRT requirements in effect on 5/1/24 | 4/1/25 [§2.9.1.2(9)]

## Slide 9: Voltage Ride-Through

## Slide 10: NOGRR245 Review of Requirements & Dates
Requirement | Deadline
All Resources: Until maximized FRT/VRT capability, comply with all ride-through requirements in effect 5/1/24 | Until maximization [§2.11(2)]
If RE learns of new available software, firmware, settings, or parameterization modification for Resource w/ exemption, it must: (i) submit plan to implement modifications w/n 90 days and (ii) if ERCOT approves plan, implement it w/n 180 days | On-going [§2.12.1(7)]
Resources must inform ERCOT of date they fully maximized FRT/VRT capability to equipment limits to meet/exceed (as applicable): §2.6.2.1(1)-(5) IEEE 2800-2022 §§5, 7 and 9 §2.9.1.1(1)-(7) §2.9.1.2(1)(-(7) | Upon maximization [§2.6.2.1(6); §2.9.1(8); §2.11(3)]
Resource that believes it: (i) already maximized FRT/VRT capabilities to meet/exceed applicable requirements, or (ii) will maximize FRT/VRT capabilities to meet/exceed requirements before 12/31/25, must submit accurate models reflecting field settings consistent w/ requirements for model updates in Protocols and Other Binding Documents | When informing ERCOT of maximization [§ 2.11(1)]

## Slide 11: Recap
All Resources must maximize – to the fullest extent possible – FRT and VRT capability and not merely meet minimum ride-through requirements
AResource that cannot meet applicable FRT/VRT requirements even after maximizing must – by 4/1/25 - submit:
  extension request and/or
  exemption request
  IFRTCR or IVRTCR(as applicable)
  Description of need for extension/exemption
  Comply w/ ride-through requirements in effect on 5/1/24 until ride-through capability maximized

## Slide 12: General Information
  ERCOT 1/8/25 Market Notice
    M-A010825-01 Implementation of Requirements in Nodal Operating Guide Revision Request (NOGRR) 245, Inverter-Based Resource (IBR) Ride-Through Requirements
  NOG requirements in effect on 5/1/14
  https://www.ercot.com/files/docs/2024/04/26/May%201,%202024%20Nodal%20Operating%20Guide.pdf
  Public Utility Commission working on a rulemaking on the process of requesting exemptions (Project #57374)

## Slide 13: Questions
?