## NPRR_1272 Clarification
| Generator +/- 0.95 PF @ Gen Terminals or Low Side of MPT | [6 empty] | Transmission Level PUN Load
| Gen | 100 | MW |  |  | Load | -50 | MW
| PF | 0.95 | (Lagging) |  |  | PF | -0.95 | as Required by Tariff
| MVAR | 32.8684 |  |  |  | MVAR | -16.4342
Private Use Network Facilities
IRR 10% Case: Use PF of .291
POIB
|  | Net To Grid | 50 | MW
|  | Net Reactive | 16.4342 | MVAR
|  | PF | 0.95 |  | TSP Facilities
ERCOT Grid
EPS Meter

## Current Interpretation
| Generator +/- 0.95 PF @ Gen Terminals or Low Side of MPT | [6 empty] | Transmission Level PUN Load
| Gen | 100 | MW |  |  | Load | -50 | MW
| PF | 0.89692 | (Lagging) |  |  | PF | -0.95 | as Required by Tariff
| MVAR | 49.3026 |  |  |  | MVAR | -16.4342
Private Use Network Facilities
IRR 10% Case: Use PF of .291
POIB
|  | Net To Grid | 50 | MW
|  | Net Reactive | 32.8684 | MVAR
|  | PF | 0.83562 |  | TSP Facilities
ERCOT Grid
EPS Meter