## Slide 1
February 27, 2025
Technical Advisory Committee
Nitika Mago
Balancing Operations Planning Staff
Operational Experience from Nov 10, 2024 With Focus on ESRs
And
Introduction to NPRR 1273

## Slide 2: Introduction
November 10, 2024 was a day when offline Non-Spin and SCED-dispatchable ECRS was released and stored energy from Energy Storage Resources (ESRs) was relied upon to serve load for several consecutive hours.
  System wide State of Charge (SOC) declined to an all-time minimum value of 1,460 MWh (~11.61%) at 9:03 pm.
This slide deck shares analysis that ERCOT has conducted for this day, ERCOT’s observations that led to the need for NPRR1273, Appropriate Accounting for ESRs in PRC Calculation and some additional outreach that ERCOT has started conducting.

## Slide 3: Projections
November 10, 2024 was expected to be a somewhat tight day due to generation outages and unusually low wind.
  ERCOT had issued an Advanced Action Notice on November 7 for Monday, November 11, but QSEs informed ERCOT that there were no Generation Outages that could be delayed or restored
Based on forecasted load and submitted Current Operating Plans (COPs) at 1030 am it was expected that ESR capacity would be relied upon to serve load beginning 1600.
From a commitment perspective, all available generation was online or providing Ancillary Services. Three units that had been on outage became available on Nov 10, but could not be started in time for that evening
Available Supply Forecast
Demand Forecast
Total online Thermal Capacity (COP)
Solar Forecast
Wind Forecast
Total ESR Capacity (COP)

## Slide 4: Operations
As net load increased, ESR started discharging around 4 pm. ESR net injection peaked around 5:51 pm at 4,265.8 MW.
Approximately 9,247 MWh amount of energy was injected into the grid over a 4-hour period beginning 4:21 pm. ESR State of Charge (SOC) declined from 10,707 MWh (~92.73%) to a minimum value of 1,460 MWh (~11.61%) at 9:03 pm.

## Slide 5: Observation 1: Impact of 15-minute duration on PRC
PRC counts ESR headroom that can be sustained for 15 minutes. Between 6pm and 10pm, PRC (red line) stayed well above EEA trigger levels. At 9:03 pm when system wide SOC was the lowest, there was about 3,400 MW of headroom from ESRs (~55.38% of total PRC) being accounted in PRC
Key Takeaway: On Nov 10th PRC wasn’t a good indicator of how close to the edge the system was operating. From the perspective of energy needs during an EEA Level 3 event, accounting headroom that can be sustained for 15 minutes may not give sufficient time for manual actions.
Percentage of PRC from ESRs 9:03 pm = 55.38%
Min PRC @ 6:58pm 5206 MW 2549 MW (~49%) ESRs 504 MW (~10%) Generation 195 MW (~4%) Synchronous Cond Hydros 1726 MW (~34%) Load Resources 231 MW (~4%) FFR

## Slide 6: NPRR 1273 - Introduction
North American Electric Reliability Corporation (NERC) Reliability Standard EOP-011 specifies that a Balancing Authority will declare EEA Level 3 when a system’s operating reserves are less than its Most Severe Single Contingency (MSSC) as defined by NERC, and will immediately take actions, including manual load shed, adequate to mitigate this emergency.
  ERCOT monitors PRC and will implement EEA Level 3 and shed firm load if PRC drops below 1,500 MW and is not expected to recover within 30 minutes.
  When ERCOT orders Transmission Operators (TOs) to implement load shed, they have up to 30 minutes to implement their share of that load shed amount.
During tight operational conditions when demand approaches the available supply, Ancillary Services reserves are released to be used as needed to provide energy to meet Demand.
  Under these conditions, the calculation of PRC becomes critically important.
  While the 15-minute duration in PRC was tied to the duration for the provision of Primary Frequency Response, when the value of PRC becomes most important, the calculation of PRC should include the capacity from ESRs that is able to be sustained long enough to allow time for load to be shed and not just what is needed to support frequency.
    When ERCOT orders Transmission Operators (TOs) to implement load shed, they have up to 30 minutes to implement their share of that load shed amount.
  Hence, ERCOT is proposing 45 minutes to account for control room response, rapid changes in PRC, and delays in SOC telemetry changes.
This NPRR does not impact requirements for ESRs and is only intended to change ERCOT’s PRC calculation.

## Slide 7: Observation 2: Some ESRs struggled to follow dispatch at low SOC
Towards late evening, when operating at lower SOC levels, some ESRs struggled to follow their expected set point (UDBP + Regulation). Headroom from such ESRs was adding capacity into PRC that was likely not available.
Separation between MW (blue line) and expectation (grape line)
Separation between MW (blue line) and expectation (grape line)
Key Takeaway: ERCOT has started monitoring operations of ESRs when lower SOC levels and is issuing RFIs to better understand the underlying drivers for this behavior.
Notes: In some cases, the separation between HSL and MW was getting counted as available headroom. If separation was a result of operational issues, ERCOT’s PRC maybe incorrect.

## Slide 8: Observation 3: Low SOC for up AS Responsibility
At 4 pm ESRs had sufficient SOC to meet their up AS obligation. However as net load increased and AS capacity was released, beginning 7 pm, ESRs carrying up AS Responsibility did not have sufficient SOC (green line) to meet the requirements (grape line). Further, during this evening the total SOC across all ESRs within a QSE’s fleet (blue line) during several instances was not sufficient to fulfil the SOC required to cover the up AS responsibility (blue line) ESRs were carrying at the time.
SOC Requirement: Total SOC required to fulfil up AS responsibility on ESRs for remainder of the hour.
ESR AS Providers SOC : Total SOC of ESRs carrying up AS responsibility.
QSE AS Providers ESR SOC: Total SOC from ESRs in a up AS carrying QSE’s portfolio whether or not the ESR was carrying AS.
ESR SOC: Total SOC of all ESRs
15m
30m
25m
11m
7m
Key Takeaway: Beginning 7 pm, there were several intervals where stored energy across all ESRs was not sufficient to fulfill the up AS ESR were carrying. RTC will fix this issue by either automatically moving AS to capable Resource or by not assigning AS.

## Slide 9: Summary
November 10 was a tight operating day due to outages and unusually low wind. As the sun set and net load started rising, offline Non-Spin and SCED-dispatchable ECRS was released, and Energy Storage Resources (ESRs) were relied upon for a period of 4 hours to continue serving load.
Analysis from this day highlighted the need to revisit duration accounting of ESR energy in PRC. Consequently, ERCOT has submitted NPRR 1273, Appropriate Accounting for ESRs in PRC Calculation to update duration that PRC uses for accounting headroom from ESRs.
Further the observations of low SOC for up AS analysis helped highlight operational efficiencies that would will be gained when RTC with SOC accounting is implemented.