Business Procedures

Load Resource Qualification

Non-Controllable Load Resource

Qualification and Testing Procedure

Version 2.0

January 16, 2026

Document Revisions

| Date | Version | Description | Author(s) |
| --- | --- | --- | --- |
| 8/15/08 | 0.01 | Initial draft | Steve Krein |
| 10/8/09 | 0.02 | Revised to incorporate retirement of Resources and changes to facilities | Steve Krein |
| 6/30/10 | 0.03 | Revised to incorporate remaining flow diagram elements | Steve Krein |
| 11/30/10 | 1.0 | Revised and Approved for Nodal Go Live | Paul Wattles, Mark Patterson |
| 4/1/2011 | 1.1 | Revised to Update Telemetry Test Plan | Steve Krein |
| 6/10/2023 | 1.2 | Revised to incorporate ECRS Test Requirements and other updated material | Steve Krein |
| 11/5/2024 | 1.3 | Revised to incorporate changes for dispatch done by an XML only instruction and other requirements from recent NPRRs. | Steve Krein/Anthony Pataray |
| 3/2/2025 | 1.4 | Updated the to clarify the procedure for increasing AS qualification amounts after a limit increase and added the requested MW amount to the qualification affidavit. | Anthony Pataray |
| 12/5/2025 | 2.0 | Updated for the implementation of RTC+B and measurement of NCLRs within a PUN. | Mark Patterson/Anthony Pataray |

Document Approvals

| Date | Approved By | Approval Documented In (select) |
| --- | --- | --- |
|  | <Mark Patterson> <Manager Demand Integration> | ___ Approval email on file ___ Signature Mark Patterson |

Table of Contents

1.	Introduction	2

1.1.	Purpose	2

1.2.	Protocols References Summary	2

1.3.	Operating Guide References	2

1.4.	Acronyms	3

2.	Initial Qualification	3

2.1.	Resource Asset Registration	3

2.2.	One Line Diagrams and Drawings	3

2.3.	Under-frequency Relay Requirements and Testing	3

2.4.	Provisional Qualification of Load Resources	4

2.5.	Qualification Testing for New Load Resources	5

3.	Periodic Testing and Recertification of Load Resources	6

3.1	Annual Telemetry Testing	6

3.2	Biennial UFR Recertification of Load Resources	6

3.3	Annual Recertification Testing of Load Resources	6

3.4	Performance Review of NCLRs	6

4.	Change Control and Retirement of Load Resources	7

4.1.	Change Control for Load Resources	7

4.2.	Retirement of Load Resources	7

5.	Documentation and Reports	8

5.1.	Request for Provisional Qualification and Affidavit	8

5.2.	Load Resource Qualification Test Report	10

5.3.	Qualification Test Affidavit	12

5.4.	ERCOT Non-Controllable Load Resource Under Frequency Relay Test Report	13

# Introduction

## Purpose

This document contains the procedures for how Non-Controllable Load Resources (NCLRs) register and qualify to provide Ancillary Services to the ERCOT Market. A separate business procedure governs the qualification and testing of Controllable Load Resources (CLRs).  NCLRs that are covered by this business procedure are those Loads that meet the requirements in the Protocols to register and qualify to provide Responsive Reserve Service (RRS), Non-Spinning Reserve Service (NSRS) and ERCOT Contingency Reserve Service (ECRS).  This procedure is intended to provide detailed instructions that will be used to initially test the operability of NCLRs to provide those services and to document the results of any testing that is conducted by ERCOT Staff. Once qualified, NCLRs are subject to periodic testing and a performance review for events that are specified in the ERCOT Protocols and Operating Guides.

## Protocols References Summary

| ERCOT Protocols affected Sections | 3.17 Ancillary Service Capacity Products 3.17.2 Responsive Reserve Service 3.17.3 Non-Spinning Reserve Service 3.17.4 ERCOT Contingency Reserve Service 3.18 Resource Limits in Providing Ancillary Service 8.1.1.1 Ancillary Service Qualification and Testing 8.1.1.2 General Capacity Testing Requirements 8.1.1.2.1 Ancillary Service Technical Requirements and Qualification Criteria and Test Methods 8.1.1.2.1.2 Responsive Reserve Service Qualification 8.1.1.2.1.3 Non-Spinning Reserve Qualification 8.1.1.2.1.7 ERCOT Contingency Reserve Service Qualificiation 8.1.1.4 QSE Ancillary Service Energy Deployment Compliance Criteria 8.1.1.4.2 Responsive Reserve Energy Deployment Criteria 8.1.1.4.3 Non-Spinning Reserve Service Energy Deployment Criteria 8.1.1.4.4 ERCOT Contingency Reserve Service Energy Deployment Criteria |
| --- | --- |

## Operating Guide References

| ERCOT Operating Guide Affected Sections | 2.3.1 Responsive Reserve 2.3.1.2 Additional Operational Details for Responsive Reserve Providers 2.3.2 Non-Spinning Reserve Service 2.3.2.1 Additional Operational Details for Non-Spinning Reserve Service Providers 2.33.3.1 Additional Operating Details for ERCOT Contingency Reserve Service (ECRS) Providers 3.4 Load Resource Testing Requirement 8 Attachments 8G Load Resource Tests |
| --- | --- |

## Acronyms

ECRS	ERCOT Contingency Reserve Service

IDR	Interval Data Recorder

LPC	Low Power Consumption

MIS 	Market Information System

MPC	Maximum Power Consumption

NOIE 	Non-Opt-In Entity

NSRS	Non-Spinning Reserve Service

PUN	Private Use Network

QSE	Qualified Scheduling Entity

RIOO	Resource Integration and Ongoing Operations

RRS	Responsive Reserve Service

SAMR	Special Action Modeling Request

TAC	Technical Advisory Committee

UFR	Under-Frequency Relay

XML	eXtensible Markup Language

Initial Qualification

## Resource Asset Registration

Resource Entities must first register their NCLRs using the RIOO application. The ERCOT Demand Integration team will coordinate with other ERCOT teams to ensure that the Load Resource Registration information is valid.

## One Line Diagrams and Drawings

Resource Entities must submit a simplified one-line diagram that shows the NCLR, and non- load resource load, associated interconnecting hardware and a brief description of the type of NCLR load to ERCOTLRandSODG@ercot.com. If the NCLR is operating as part of a PUN, a diagram of the PUN and all connected generation units as well as any other major loads should also be included.

The Demand Integration team will review that drawing and ensure that it contains at a minimum:

- Name, Load Type, and Rated Capacity

- Interrupting Device (Circuit Breaker, Oil Switch, etc)

- UFR Type, Manufacturer, and Serial Number (if applicable)

- ESID with location of 15-minute interval Settlement meter

- Transformer, including High and Low Voltages

- Substation Name and TDSP as shown in the Network Operations Model

- Feeder and Bus IDs

## Under-frequency Relay Requirements and Testing

NCLRs registering to provide service for RRS are required to have an Under-frequency Relay (UFR). NCLRs providing Ancillary Services must meet the following UFR requirements:

- To carry RRS: UFR must be 'Armed'

- To carry NSRS: UFR must be 'Unarmed'.

- To carry both RRS and ECRS: Relay must be 'Armed'.

- To carry only ECRS: UFR can be either 'Armed' or 'Disarmed'.

The initiation setting of the automatic under-frequency relay shall not be lower than 59.70 Hz with a delay time of no greater than 20 cycles. NCLRs are required to have these relays tested prior to being put in service and must submit a Relay Test Report as part of the initial registration process as well as to meet the biennial test requirement reflecting the results of that the test.  The test report shall show:

- Name, Manufacturer and Serial Number for the Relay

- Test Equipment Used to Test the Relay

- Date of the Test

- Settings for the Relay

  - As Found Test Results

  - As Left Test Results

- Name of the Person Performing the Test

The template for submitting this information can be found in Section 5.4.

## Provisional Qualification of Load Resources

Resource Entities may request that their NCLRs be provisionally qualified to provide one or more Ancillary Services. To request provisional qualification the Resource Entity must submit an Affidavit Requesting Provisional Qualification appropriate to the Service they intend to provide (RRS, ECRS or NSRS). The Request for Provisional Qualification and Affidavit form is available in section 5.1 of this procedure. The Provisional Qualification will be good for 90 days from the time it is approved and issued. During the provisional qualification period the NCLR will be required to perform an NCLR Qualification Test for the Services they plan to provide. The Demand Integration Team will review the application to ensure that it is complete. The following checklist will be used to determine whether a Provisional Qualification will be approved.

- Resource Entity (RE) Registration is complete and has been filed with ERCOT Legal

- QSE Acknowledgement is complete and on file with ERCOT Legal

- Partnership established in ERCOT Settlements Systems between the RE and QSE.  The partnership is required to be in place at least 45 days prior to the provisional qualification start date.

- RIOO submission is complete and has been submitted using a Digital Certificate for the Resource Entity.

- Telemetry is in place and tested from the QSE to ERCOT showing:

- Load Resource net real power consumption in MW (NPF)

- Any data mutually agreed to by ERCOT and the QSE to adequately manage system reliability

- Load Resource breaker status

- UFR Status, Enabled or Disabled, if there is no UFR show a status of Disabled.

- LPC in MW

- MPC in MW

- Ancillary Service Capability point for RRS

- Ancillary Service Ramp Rates for ECRS and NSRS

- Resource Status Code

- Affidavit for provisional qualification of Loads to provide RRS, ECRS and/or NSRS is executed and provided to the ERCOT Demand Integration Team.

Once the NCLR is in the model, the Demand Integration Team will confirm all telemetry appears to be active and functioning correctly and notify the Resource Entity and QSE that the NCLR has been provisionally qualified.

## Qualification Testing for New Load Resources

Once the NCLR meets all pre-qualification requirements and is set up in ERCOT systems, it’s ready to request an Ancillary Service qualification test. The QSE coordinates the test by scheduling a date with the Resource Entity and ERCOT’s Demand Integration Team. ERCOT will then establish and communicate an 8-hour window for the test. For resources with a Provisional Qualification, the test must be completed within 90 days, or the qualification will be forfeited with no extensions granted.

A successful deployment initiated by an ERCOT Operator during this provisional period may be accepted in place of a test.

During the test window, the Load Resource should be online and have enough capacity (NPF) to meet the amount requested for Ancillary Service qualification. Leading up to the test, the load resource may participate in DAM at the discretion of the QSE. Should the QSE choose to participate, the QSE must telemeter the proper capability or applicable ramp rates. If not, telemetry should be updated during a pre-test Telemetry Checkout. The ERCOT test coordinator will guide the setup to ensure the resource can be dispatched via XML instruction, which includes an initial deployment, possible redeployment, and recall instructions.

The test will involve a Load interruption lasting around 45-60 minutes, covering deployment ramp-up and sustained response time, followed by an ERCOT-issued XML recall instruction. The NCLR’s response will be measured by comparing its pre-deployment baseline load, averaged over a 5-minute interval before the XML instruction. Afterward, the QSE should restore the NCLR to its pretest status. The ERCOT Test Coordinator will use ICCP Data to complete the test report (Section 5.2).

For the test to be successful, the NCLR’s response must meet three criteria:

- Load deployed within 10 minutes (RRS/ECRS) or 30 minutes (NSRS).

- Load response between 95% and 150% of the instructed MW value.

- For NCLRs located within a Private Use Network (PUN) ERCOT will perform a secondary verification to ensure the required response was delivered at the PUN’s Point of Interconnect (POI) within the ERCOT transmission system. To perform this secondary verification ERCOT may use a combination of telemetry at various points within the PUN and POI as well as using settlement meter data available for the PUN. This same secondary verification may be performed by ERCOT following any ancillary service deployments from the resource.

If the test is successful, ERCOT’s Demand Integration Team will notify ERCOT personnel and the QSE that the NCLR is qualified to provide RRS, ECRS, or NSRS in the Ancillary Services Markets, with a report copy provided as outlined in Section 5.2 along with a Qualification Test Affidavit found in Section 5.3.

If the NCLR does not pass, its Provisional Qualification will be revoked, and the Load Resource will be ineligible for Market Activities until it successfully completes a re-test, with the updated report also provided per Section 5.2.

# Periodic Testing and Recertification of Load Resources

## Annual Telemetry Testing

Per ERCOT Protocol Section 8.1.1.2, all Load Resources providing RRS or ECRS with a high-set under-frequency relay are subject to an annual test of the telemetry associated with that Load Resource. The telemetry test will be based on the actual operation of the Load Resource and include a verification of the telemetry attributes.

QSEs are allowed to use an actual Load Resource deployment to confirm that their telemetry is in agreement with the ERCOT system values. The RE/QSE should submit their test results to ERCOTLRandSODG@ercot.com using the Annual Telemetry Test Report found in Nodal Operating Guide Section 8 – Attachment G: Load Resource Tests.

## Biennial UFR Recertification of Load Resources

Per ERCOT Protocol Section 8.1.1.2, all NCLRs with Hi-Set Under-Frequency Relays will be required to have their UFRs tested every two years to verify that the relays are set in accordance to section 2.3.1.2 (6) of the ERCOT Nodal Operating Guides. If the relay responds to an actual frequency event and the Load trips off-line, that event may be used in lieu of an actual test of the relay. The RE/QSE should submit their test results to ERCOTLRandSODG@ercot.com using the Biennial Test for Load Resources Providing Responsive Reserve Service found in Nodal Operating Guide Section 8 – Attachment G: Load Resource Tests.

## Annual Recertification Testing of Load Resources

All NCLRs that are qualified to provide RRS, ECRS, and NSRS will be subject to an annual recertification test. If an NCLR has performed satisfactorily during the previous 365-days to a Load Resource XML deployment instruction that was initiated by an ERCOT Operator during an emergency condition, that performance may be used in lieu of an actual interruption test. The results of the testing will be documented on the Load Resource Qualification Test Report indicating that the test type was an Annual Recertification Test. That test report is shown in Section 5.2 of this Procedure.

## Performance Review of NCLRs

Monthly Performance Reports—Monthly performance reports are prepared, broken down for each Ancillary Service, and posted for QSE and Resource Specific evaluation of the NCLRs. These automated reports are posted to the MIS.

Performance during Under-Frequency Events—NCLRs may be evaluated by ERCOT working with a designated Working Group (PDCWG) for resources requiring Load response via a UFR for all frequency events when frequency gets near or below 59.7 Hz.

Compliance Performance Review—the ERCOT Demand Integration team will identify those NCLRs that are failing to meet Protocol requirements.  NCLRs that fail to meet performance requirements specified in Section 8 of the Protocols may be suspended from further participation for up to 6 months. To be requalified these NCLRs must identify the cause, develop a corrective action plan, and then be subject to passing a new set of qualification tests. Corrective Action plans should be submitted to ERCOTLRandSODG@ercot.com. The manager of the ERCOT Demand Integration team will review and approve all Corrective Action Plans.

# Change Control and Retirement of Load Resources

## Change Control for Load Resources

If a Resource Entity makes a change to the operational parameters of a Load Resource, it is required to submit a revision in RIOO so ERCOT can make the associated changes in the Network Model. Depending on the nature of the change, the Resource Entity may need to submit a new one-line diagram and UFR test report. If the Resource Entity or Qualified Scheduling Entity also requests an increase to the Load Resources Ancillary Service Qualification (ASQ) amount, a Qualification Test may be required to confirm control of the increased capacity. A test is required if the Load Resource's ASQ increases by at least 5 MW or 20% of its current ASQ, whichever is greater.

To verify the new Ancillary Service Qualification amount, a self-test must be scheduled with the Demand Integration team who will coordinate directly with the ERCOT Control Room. A one-hour window will be mutually agreed upon at least 24 hours prior to the start of the test. The Load Resource will be required to demonstrate curtailment of the increased capability within the one-hour window. Successful curtailment will allow the Demand Integration team to increase an existing Load Resource’s AS Qualification amount.

## Retirement of Load Resources

When a Load Resource decides to discontinue participation in the ERCOT Ancillary Service Market, its Resource Entity will submit a revision to RIOO that will indicate a new stop date for the Load Resource. Demand Integration staff will coordinate with the EMS, Network Model and Settlements staff to remove the Load Resource from the ERCOT software systems.

# Documentation and Reports

## Request for Provisional Qualification and Affidavit

STATE OF TEXAS		§					§

COUNTY OF TRAVIS	§

AFFIDAVIT

(For requesting provisional qualification of load resources to provide Ancillary Services)

BEFORE ME, the undersigned authority, ________________, being first duly sworn, deposes and states:

- “My name is      .  I am over the age of twenty-one and am competent to make the following statements.

- I am employed as       at [Entity], having its principal place of business at      .

- [Entity] is requesting that ERCOT provisionally certify the load known to ERCOT as       (“the Load”) as a Resource, pursuant to Section 8.1.1.1(4) of the ERCOT Protocols for the following Ancillary Services (check all that apply:  ☐Responsive Reserve Service, ☐ ERCOT Contingency Reserve Service and, ☐ Non-Spinning Reserve Service. The maximum interruptible load for this provisional qualification will be _______MW.

- I have reviewed and fully understand Section 8.1.1.1(4) of the ERCOT Protocols.

- I acknowledge that the provisional qualification to provide the above requested Ancillary Service(s) which [Entity] is requesting is valid for a period of ninety (90) days from the date provisional qualification is awarded.

- I also acknowledge that if either (a) during the provisional qualification period the Load does not successfully provide the above requested Ancillary Service(s) when required, or (b) after the provisional qualification period the Load has not successfully completed its qualification as per the above requested Ancillary Service(s) Qualification document, then in either event, the Load will no longer be qualified to provide the service.

The foregoing statements offered by me are true and correct and the opinions stated therein are, in my judgment and based upon my professional experience, true and correct.”

______________________________

Affiant

SUBSCRIBED AND SWORN TO BEFORE ME on this ______ day of _______________, 20__, by _____________________, Affiant named herein.

___________________________________

Notary Public, State of Texas

## Load Resource Qualification Test Report

RESULTS of LOAD RESOURCE ANCILLARY SERVICE TESTING

Test Date:					Dispatch Asset Code:

Resource Entity: 				QSE:

TDSP: 					Transmission Substation name:

Registered Capacity (MW):

Type of Ancillary Service Test:

Pre-deployment Telemetry

|  | QSE Reported Value | ERCOT Reported Value |
| --- | --- | --- |
| LR Net real power Flow (MW) |  |  |
| Resource Status Code |  |  |
| AS Capability (MW/Ramp Rate) |  |  |
| MPC |  |  |
| LPC |  |  |
| Breaker Status |  |  |
| UFR Status |  |  |

Time for XML Deployment Instruction from ERCOT:

Required Deployment Time to respond to instruction from ERCOT:

Load Resource responded at:

Dispatched Capacity (MW): 	Load Response (MW): (% of XML Instruction)

Load Response based on TDSP Telemetry Delta Change:

Post-deployment Telemetry

|  | QSE Reported Value | ERCOT Reported Value |
| --- | --- | --- |
| LR Net real power Flow (MW) |  |  |
| Resource Status Code |  |  |
| AS Capability (MW/Ramp Rate) |  |  |
| MPC |  |  |
| LPC |  |  |
| Breaker Status |  |  |
| UFR Status |  |  |

LR Deploys within 10 minutes of XML:  Pass		Fail

LR Remains Deployed during Entire Deployment Period:  	Pass		Fail

LR Time of Recall XML Instruction: ______________________

Time Load Restored to Pretest Conditions:  ___________________

Limiting Factors if Any: 	_______________________

ERCOT Testing Coordinator:	_______________________

QSE Representative Initiating Load Shed:      ________________________

Signature:  _____________________________

LR Authorized Representative: _________________________________

Signature:  _____________________________

## Qualification Test Affidavit

STATE OF TEXAS		§

§

COUNTY OF TRAVIS		§

AFFIDAVIT

Load Qualification Tests for Load Resources providing Responsive Reserve Service (RRS) or ERCOT Contingency Resource Service (ECRS) or Non-Spinning Reserve Service

BEFORE ME, the undersigned authority, ________________, being first duly sworn, deposes and states:

- “My name is_________________.  I am over the age of twenty-one and am competent to make the following statements.

- I am employed as ___________________ at _______________________________, having its principal place of business at _________________________________.

- I have reviewed and fully understand the Load Resource Ancillary Service Qualification Test Procedures that govern load participation in the ERCOT Ancillary Service Markets.

- I hereby affirm and certify that the method used to dispatch and shed the load as part of that test is consistent with the method that will be used during an actual deployment of the Load Resource named ______________.

- I hereby affirm and certify that the facilities described in the Resource Entity’s Asset Registration, One-line diagram and if applicable the Under-Frequency Relay Test Report; attached hereto are to the best of my knowledge in compliance with all requirements specified in the ERCOT Protocols and Operating Guides.

- The test results are attached to this Affidavit and represent an accurate assessment of the testing that was conducted and are a part of this Qualification Test documentation.

The foregoing statements offered by me are true and correct and the opinions stated therein are, in my judgment and based upon my professional experience, true and correct.”

______________________________

Affiant

SUBSCRIBED AND SWORN TO BEFORE ME on this ______ day of _______________, 20__, by _____________________, Affiant named herein.

______________________________

Notary Public, State of Texas

## ERCOT Non-Controllable Load Resource Under Frequency Relay Test Report

Customer Name (RE):      _____________________

Site Common Name:        _____________________

ESI ID or UMI:                  _____________________

LR Dispatch Asset Code: _____________________

Test Equipment Used:      _____________________

Underfrequency Relay Info

Manufacturer:       _____________________

Model:                   _____________________

Serial:                   _____________________

Relay Settings

Test date:                       ______________________

Tested by:

Company:            ______________________

Street:                  ______________________

City, State Zip:     ______________________

Phone:                 ______________________

Inspector:             ______________________

Signature: