## Slide 1
PGRR122
PLWG
March 18, 2025
Jeff Billo
ERCOT Operations Planning

## Slide 2: PGRR122 Update
DWG and PLWG Feedback
Feedback | ERCOT’s Response
Frequency instability due to loss of large, voltage sensitive loads is a valid reliability concern. | ERCOT agrees.
The existing dynamic models do not properly represent the voltage sensitive nature of data centers. Hence, the studies will not show a criterion violation. | ERCOT recommends using voltage protection settings in the models that correspond to recent data center trip events if reliable customer model data is not available. ERCOT and TSPs should continue to work through DWG to ensure appropriate models are used in the studies. ERCOT is working with industry and research partners to improve the models.
Recent studies show that there may existing locations on the system where a fault will cause more than 1,000 MW of load to trip. If PGRR122 is implemented immediately, then there will be existing criteria violations that will be difficult to solve with transmission upgrades. | ERCOT proposes to: Implement PGRR122 immediately for large load interconnection studies; and Gray box the language for all other studies (annual planning analysis) until January 1, 2028. This will allow time to develop solutions for any “existing” criterion violations.

## Slide 3: PGRR122 Next Steps
ERCOT proposes to move forward with PGRR122:
  Modify LCRA comments by adding a gray box for all non-LLI studies
  Make clarifying edits to LCRA comments (see posted draft comments)
  Update the 1,000 MW limit before TAC approval based on results from ERCOT’s Frequency Overshoot Study (tentatively planned to share results in April)

## Slide 4
Questions?

## Slide 5: PGRR122 Background
Southern Cross Directive 9 Study showed that the loss of 1,488 MW of demand during certain system conditions could cause frequency to exceed 60.6 Hz, which could lead to generator tripping and frequency instability
  NPRR1034 approved to limit DC tie exports (and imports) for frequency stability
https://www.ercot.com/files/docs/2021/07/07/AS_Impact_and_Overshoot_Study_Report_v14_Final.docx
Scenario Name | Inertia (GW·s) | Load (GW) | Wind (GW) | Synchronous Gen (GW)
Scenario 0 | 130 | 34 | 15.5 | 19
Scenario 1 | 130 | 34 | 10 | 24.5
Scenario 2 | 130 | 32 | 5 | 27.5
Scenario 3 | 130 | 32 | 3.5 | 29
Scenario 4 | 120 | 29.9 | 3.5 | 26.9
Scenario 5 | 110 | 27.2 | 3.5 | 24.2
 | Scenario 0 | Scenario 1 | Scenario 2 | Scenario 3 | Scenario 4 | Scenario 5
Highest Frequency Overshoot (Hz) DR=2.0 | 60.38 | 60.47 | 60.51 | 60.53 | 60.60 | 60.70
Highest Frequency Overshoot (Hz) DR=0.0 | 60.42 | 60.54 | 60.60 | 60.62 | 60.73 | 60.89

## Slide 6: PGRR122
Problem Statement:
  Several Large Load interconnection (LLI) requests that exceed 1,000 MW and multiple areas with smaller LLI that in aggregate exceed 1,000 MW
  ERCOT has observed poor voltage ride through capability of Large Loads: https://www.ercot.com/files/docs/2024/11/18/ERCOT%20Large%20Load%20Events_PDCWG_19Nov2024.pdf
  Southern Cross study showed that there is a frequency stability limit for the amount of demand that can be lost under contingency
  Large Loads do not register as an ERCOT Market Participant, so ERCOT cannot curtail them in real-time (like a DC tie)
Proposed Solution:
  Establish a maximum amount of load (MW) that can be lost under contingency to maintain frequency stability
    Conduct a study to determine maximum loss of load limit
    Based on the Southern Cross study limit of 1,488 MW, and considering a margin to account for system changes, set the limit to be 1,000 MW initially