## Slide 1
ERCOT Frequency Control Report
March 2025
ERCOT
Operations Planning
PDCWG | April 16th , 2025

## Slide 2: Summary of March 2025
CPS1: 175.89 %
Current CPS1 12-Month Rolling Average: 176.3 %
0 BAAL Exceedance(s)
0 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2023
2023 BAAL-003 FRM Performance: -1130.21
2025 RMS1 Statistics
  Mean: 14.18 mHz
  Min: 11.86 mHz
  Max 18.32 mHz
Energy Statistics
  Total Energy: 35,208,781 MWh
  Wind Energy: 12,055,131 MWh
  Percent Energy from Wind: 34.24 %
  Solar Energy: 5,143,399 MWh
  Percent Energy from Solar: 14.61 %
Minimum System Inertia
  Mean: 154,700 MW*s
  Max: 224,372 MW*s on March 24th
  Min: 118,032 MW*s on March 18th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Mar-25 CPS1 (%): 175.89
Notes: CPS1 Score is 175.89%
Scores Below 100%: 89.94% on Mar 5th at 17:00 and 97.28% on March 12th at 16:00
1. 89.94 @ 3/5/2025 17:00
Expected Generation Deviation: The expected generation deviation remained negative throughout this hour with significant contribution from solar. The solar
generation ramped down by ~15000 MW during his hour.
Regulation: ~692 MW of Regulation Up was deployed and exhausted during this period.
SCED Offsets: Multiple manual GTBD SCED offsets were applied during this period with highest being 500 MW.
2. 97.28 @ 3/12/2025 16:00
Expected Generation Deviation: The expected generation deviation remained negative during second part of the hour with significant contribution from solar generation. The solar
generation ramped down by ~3000 MW between 4:35 PM – 5:00 PM
Regulation: ~607 MW of Regulation Up was deployed and exhausted during this period.
SCED Offsets: Multiple manual GTBD SCED offsets were applied during this period with highest being 350 MW.

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in March.

## Slide 6: 15-Minute Average CPS1%
Mar-25 CPS1 (%): 175.89
Notes: CPS1 score is above 160% for all 15-minute intervals.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average:176.3%
Notes: 12 month rolling average CPS1 score is 176.3% which is in line with expectations, and the CPS1 score for March is consistent with previous months.

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is lower compared to 2024.
  2025 Stats:
  Mean: 14.18 mHz
  Min: 11.86 mHz
  Max 18.32 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by month
14.18 mHz on avg for March 2025

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between March 2024 and March 2025. Compared to last year, there are slightly more instances of frequency hovering around the lower dead bands.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile between March 2023 and March 2025. Similar to the previous slide, compared to 2023, there are less instances of frequency hovering around the dead bands.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: Time error is negative throughout March. We have seen significant accumulation in first two weeks. ERCOT observed real-time telemetry and operational issues from wind and solar units
which effected the ERCOT frequency control. ERCOT has been working with the Market Participants to address the operational issues. ERCOT tuned the GTBD ACE integral feedback to recover the time error.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2023 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2023 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO = -471.0, FRM median = -913.56, FRM average = -992.
OP2022: FRO = -412.0, FRM median = -1060.40, FRM average = -1153.4
OP2023: FRO = -463.0, FRM median = -1130.21, FRM average = -1302.7
OP2024: FRO = -395.0,
OP2025: FRO = -455.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 35,208,781 MWh

## Slide 22: Total Energy from Wind Generation
Notes:   12,055,131 MWH

## Slide 23: % Energy from Wind Generation
Notes: 34.24% of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 5,143,399 MWh

## Slide 25: % Energy from Solar Generation
Notes: 14.61% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia in March 2025 = 118, 032 MW*s on March 18th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
March Data:
Mean: 154,700 MW*s
Max: 224,372 MW*s on March 24th
Min: 118, 032 MW*s on March 18th

## Slide 28: ERCOT Inertia 2015-2025
Date and Time | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 00:00 AM | 2022 03/21 01:00 AM | 2023 04/18 02:00 AM | 2024 03/29 03:00 AM | 2024 03/29 03:00 AM | 2025 03/18 12:00 AM
Min synch. Inertia (GW*s) | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 109 | 115 | 124 | 130 | 130 | 118.3
System load at minimum synch. Inertia (MW) | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 32,599 | 33,365 | 35,799 | 37,297 | 37,297 | 48,973
Non-synch. Gen. in % of System Load | 42 | 47 | 54 | 53 | 50 | 57 | 65 | 66 | 61 | 68 | 68 | 74
Notes: Summary of ERCOT inertia for the previous 10 years. Lowest inertia this year was on March 18th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 29: Questions?
Thank you!