## Slide 1
Resources with Power Augmentation Capacity– RTCB Telemetry
PDCWG
4/16/2025
ERCOT
Operations Analysis

## Slide 2: Introduction
RTCB improves the telemetry from Resources with Power Augmentation Capacity (offline when duct burners are not fired) by introducing new telemetry points.
  High limit of the Frequency Responsive Capacity
  Low Limit of the Frequency Responsive Capacity
  Frequency Responsive Capacity Factor
  Inactive Power Augmentation Capacity
The new telemetry points are intended to inform SCED, the Frequency Responsive Capacity of the resource to ensure that the Regulation and RRS-PFR awards are within the frequency responsive capacity. There are no frequency responsive capacity limitations when providing Non-Spin and ECRS
Currently, the onus is on the QSEs to ensure that Regulation and/or RRS-PFR is not coming from the steamer capacity and preserve sufficient headroom on GT’s. ERCOT also enforces real-time and post-hoc compliance checks. The improved telemetry will eliminate this burden on QSEs and ERCOT.

## Slide 3: Current relevant RTCB telemetry
In RTC, Resources with Power Augmentation to telemeter four new telemetry points
Telemetry | Analog | Unit | Description | What could QSE telemeter to ERCOT
Frequency Responsive Capacity High Limit | HFRL | MW | High limit of the Resource’s capacity that is frequency responsive, used by SCED to limit the Regulation and RRS-PFR awards are within Frequency Responsive capacity | Max(Sum of high MW limit of online GT’s, LSL of the online configuration)
Frequency Responsive Capacity Low Limit | LFRL | MW | Low limit of the Resource’s capacity that is frequency responsive, used by SCED to limit the Regulation and RRS-PFR awards are within Frequency Responsive capacity | LSL of the online configuration
Frequency Responsive Capacity Factor | FRQF |  | Maximum amount of total Base Point provided by the frequency responsive capacity of the resource, used by SCED to limit the Regulation and RRS-PFR awards are within Frequency Responsive capacity | Total Output of GTs/Base Point
Inactive Power Augmentation Capacity | PAUG | MW | Power Augmentation capacity that is not On-Line for Resources that have power augmentation capacity included in HSL. This is used in SCED to determine the portion of the Non-Spin award that will be provided by power augmentation capacity that is not active and deployed as offline Non-Spin. | Static unfired Power Augmentation capacity when ducts are not fired and 0 when ducts are fired
Notes: r

## Slide 4: RTCB Telemetry Example**
2x1 CC Configuration
CC component | LSL | HSL
GT1 | 75 | 100
GT2 | 75 | 100
ST3 with 25 MW unfired duct burner capacity | 25 | 150
2x1 CC Configuration | 175 | 350
Base Point | GT1+GT2 MW | ST3 MW | Freq Resp High Limit | Freq Resp Low Limit | Freq Response Factor(Total GT Output/BP) | Inactive Power Augmentation Capacity | Reg-Up + RRS Awards Feasible ** | Reg-Down Award Feasible **
200 | 150 | 50 | 200 | 175 | 0.75 | 25 | 50 | 0
250 | 166 | 84 | 200 | 175 | 0.664 | 25 | 34 | 0
275 | 174 | 101 | 200 | 175 | 0.6327 | 25 | 26 | 0
300 | 182 | 118 | 200 | 175 | 0.6067 | 25 | 18 | 7
310 | 188 | 122 | 200 | 175 | 0.6065 | 25 | 12 | 13
325 | 200 | 125 | 200 | 175 | 0.62 | 25 | 0 | 25
350 | 200 | 150 | 200 | 175 | 0.571 | 0 | 0 | 25
RTCB Telemetry
** This example is intended for illustration purpose to show RRS-PFR and Reg awards will be limited to Frequency responsive capacity and does not reflect a real scenario; Economics, Ramp Rate Limits, other constraints or limitations are ignored in this example

## Slide 5: BAL-TRE-001-2 Impact
However, this approach impacts the BAL-TRE calculations, since the current RTCB implementation for Resources with Power Augmentation capacity, deletes the existing NFRC telemetry.
The BAL-001-TRE-2, Expected Primary Frequency Response calculations excludes only the remaining/unused duct capacity, which is informed to ERCOT with NFRC telemetry. Note: PAUG telemetry in RTC is expected to be static unfired duct capacity when not fired and 0 when fired.
Retaining current NFRC telemetry in RTCB will resolve this issue.

## Slide 6: Conclusion
With the new telemetry,
  The RTC constraints will limit the Regulation and RRS-PFR awards to online GT capacity which is frequency responsive.
  ECRS and Non-Spin can be provided up to HSL , portion of the Non-Spin Award may come from Inactive Power Augmentation capacity, which is treated and deployed as Offline Non-Spin from AS Manager.
ERCOT will recommend retaining NFRC telemetry in RTCB.
Please review this approach and provide any feedback to Abhilash.MasannaGari@ercot.com before 4/28/25.

## Slide 7: Questions?