## Slide 1
PRC-028
vs IEEE 2800-2022
vs NOGRR255
Eric Newnam
Reliability Engineer, III
April 18, 2025

## Slide 2: R1 Sequence of Event Recording Data
R1. Each Generator Owner shall have sequence of event recording (SER) data for the following Elements that it owns:
1.1. Circuit breaker position (open/close) for circuit breakers associated with the main power transformer(s), collector bus(es), shunt static and dynamic reactive device(s), and AC-DC and DC-AC converters, if any, in case of VSC HVDC system with a dedicated connection to Inverter-Based Resource
1.2. For IBR units in commercial operation after the effective date of this standard, the following data shall be recorded when triggered by ride-through operation or tripping of an IBR unit
1.2.1. All fault codes
1.2.2. All fault alarms
1.2.3. High and low voltage ride-through mode status
1.2.4. High and low frequency ride-through mode status
1.3. For IBR units in commercial operation before the effective date of this standard, if capable, the following data shall be recorded when triggered by ride-through operation or tripping of an IBR unit
1.3.1. All fault codes
1.3.2. All fault alarms
1.3.3. High and low voltage ride-through mode status
1.3.4. High and low frequency ride-through mode status

## Slide 3: R1 Sequence of Event Recording Data
NOGRR255
6.1.4.1.1 Sequence of Events Recording Data Requirements
(1) Generation Resource owners and ESR owners shall have sequence of events data for all positions (open/close) for circuit breakers associated with the MPT(s), collector bus, and shunt static or dynamic reactive device(s).
Provision Data Type | Measurement/data points (as applicable) | Recording Rate | Retention | Duration | Measurement (as applicable)
Sequence of events recording (SER) data (tabular log file, time tag shall have an accuracy of one millisecond or less) | SER devices should be sized to capture and store hundreds or thousands of event records and logs. SER event records can be triggered for many different reasons but at minimum, shall include the following: - Event date/time stamp (synchronized to common reference, e.g., Coordinated Universal Time [UTC]) - Event type (status changes, synchronization status, configuration change, etc.) - Sequence number (for potential overwriting) | Static, as changed | 90 days | NA | Not applicable
Key Takeaways
IEEE-2800-2022: more general data requirements than PRC-028, future units only
NOGRR255: similar to PRC-028 for existing and future units
IEEE-2800-2022
Table 19—Measurement data

## Slide 4: R2 Fault Recording Data
R2. Each Generator Owner shall have triggered fault recording (FR) data to determine the following electrical quantities for Elements that it owns:
2.1. High-side of the main power transformer FR data:
2.1.1. Phase-to-neutral voltage for each phase
2.1.2. Each phase current and the residual or neutral current
2.1.3. Real and Reactive Power expressed on a three-phase basis
2.2. Collector feeder breaker FR data:
2.2.1. Phase-to-neutral voltage for each phase
2.2.2. Each phase current and the residual or neutral current
2.2.3. Real and Reactive Power expressed on a three-phase basis
2.3. Shunt dynamic reactive device FR data:
2.3.1. Phase-to-neutral voltage for each phase
2.3.2. Each phase current and the residual or neutral current
2.3.3. Reactive Power output expressed on a three-phase basis

## Slide 5: R2 Fault Recording Data
IEEE-2800-2022
Table 19—Measurement data
Provision Data Type | Measurement/Data Points (as applicable) | Recording Rate | Retention | Duration | Measurement (as applicable)
Digital fault recording (DFR) data (COMTRADE format and tabular log file) | This data shall be captured for at least the plant-level (e.g., at the point of measurement) response to BPS events. It is typically high resolution (kHz) point-on-wave data (transient) and triggered based on configured settings. Data points shall include: - Time stamp - Phase-to-ground voltage for each phase - Bus frequency (as measured/calculated by the recording device) - Each phase current and residual or neutral current - Calculated active and reactive power output - If applicable, dynamic reactive device voltage, frequency, current, and power output - Applicable binary status | ≥ 128 samples per cycle, triggered | 90 days | 5 s COMTRADE data, (split between pre-fault and post-fault data needs to be mutually agreed upon with the TS owner/TS operator) | Subclause 4.4, Table 2
NOGRR255
6.1.4.1.2 Fault Recording Data and Triggering Requirements
(1) Generation Resource owners and ESR owners shall have fault recording data to determine the following electrical quantities for each triggered fault recording record:
(a) Generation Resource or ESR level fault recording data:
(i) Time stamp;
(ii) Phase-to-neutral voltage for each phase on the high side of the MPT;
(iii) Each phase current and the residual or neutral current on the high side of the MPT;
(iv) If applicable, active and reactive power on the high side of the MPT;
(v) If applicable, frequency and rate-of-change-of-frequency (df/dt) data for at least one generator-interconnected bus measurement; and
(vi) If applicable, dynamic reactive device input/output such as voltage, current, and frequency.
(vii) Applicable binary status.
Key Takeaways
IEEE-2800-2022: general requirements similar to PRC-028, future units only
NOGRR255: similar to PRC-028 with additional data points

## Slide 6: R3 Digital Fault Recording Data Specifications
R3. Each Generator Owner shall have FR data as specified in Requirement R2 that meets the following:
3.1. High-side of the main power transformer FR data:
3.1.1. A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point
3.1.2. A minimum recording rate of 64 samples per cycle
3.1.3. Trigger settings for at least the following:
3.1.3.1. Neutral (residual) overcurrent
3.1.3.2. AC phase overvoltage and undervoltage
3.1.3.3. Over frequency and underfrequency
3.2. Collector feeder breaker FR data:
3.2.1. A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point
3.2.2. A minimum recording rate of 64 samples per cycle
3.2.3. Trigger settings for at least the following:
3.2.3.1. Neutral (residual) overcurrent, if applicable
3.2.3.2. AC phase overvoltage and undervoltage
3.2.3.3. Over frequency and underfrequency
3.3. Shunt dynamic reactive device FR data:
3.3.1. A single record or multiple records that include a pre-trigger record length of at least two cycles and a total record length of at least 2.0 seconds for the same trigger point
3.3.2. A minimum recording rate of 64 samples per cycle.
3.3.3. Trigger settings for at least the following:
3.3.3.1. Neutral (residual) overcurrent
3.3.3.2. AC phase overvoltage and undervoltage

## Slide 7: R3 Digital Fault Recording Data Specifications
Key Takeaways
IEEE-2800-2022: measurement location is more general, but sample rate is higher than PRC-028, future units only
NOGRR255: more specific ranges than PRC-028, sample rate is higher than PRC-028 for future but lower for existing units
Provision Data Type | Measurement/Data Points (as applicable) | Recording Rate | Retention | Duration | Measurement (as applicable)
Digital fault recording (DFR) data (COMTRADE format and tabular log file) | This data shall be captured for at least the plant-level (e.g., at the point of measurement) response to BPS events. It is typically high resolution (kHz) point-on-wave data (transient) and triggered based on configured settings. Data points shall include: - Time stamp - Phase-to-ground voltage for each phase - Bus frequency (as measured/calculated by the recording device) - Each phase current and residual or neutral current - Calculated active and reactive power output - If applicable, dynamic reactive device voltage, frequency, current, and power output - Applicable binary status | ≥ 128 samples per cycle, triggered | 90 days | 5 s COMTRADE data, (split between pre-fault and post-fault data needs to be mutually agreed upon with the TS owner/TS operator) | Subclause 4.4, Table 2
NOGRR255
6.1.4.1.2 Fault Recording Data and Triggering Requirements
(3) Fault recording equipment shall meet the following requirements for a Generation Resource or ESR as described in paragraph (1) above:
(a) Have either continuous data recording or triggering for at least the following:
(i) High-side of the MPT fault recording triggers and, if applicable, any dynamic reactive device FR triggers:
(A) Neutral (residual) overcurrent of 0.20 per unit (p.u.) or less of rated current transformer secondary current;
(B) Any phase under-voltage between 0.85 p.u. and 0.90 p.u., or
(1) Any phase overcurrent above 1.05 p.u. of the maximum emergency current rating, or
(2) Protective relay tripping for all protection groups;
(C) Any phase over-voltage greater that 1.10 p.u.;
(D) Frequency below 59.5 Hz or above 60.5 Hz;
(E) Frequency rate of change for low frequency of -0.08125 Hz/sec or high frequency of 0.125 Hz/sec;
(b) Minimum recording rate of:
(i) 64 samples per cycle for any Fault recording equipment installed on or replaced after June 1, 2024;
(ii) 16 samples per cycle for any Fault recording equipment installed prior to June 1, 2024; and
(c) A single record or multiple records that include pre-trigger record length of at least two cycles and a total record length of at least 2 seconds for the same trigger point.
IEEE-2800-2022
Table 19—Measurement data

## Slide 8: R4 & R5 Dynamic Disturbance Recording Data
R4. Each Generator Owner shall have continuous dynamic disturbance recording (DDR) data and storage to determine the following electrical quantities for each main power transformer(s) it owns:
4.1. One phase-to-neutral or positive sequence voltage on high-side of the main power transformer(s)
4.2. The phase current for the same phase at the same voltage corresponding to the voltage in Requirement R4, Part 4.1, or the positive sequence current
4.3. Real Power and Reactive Power flows expressed on a three-phase basis corresponding to each main power transformer(s) where current measurements are required
4.4. Frequency of any one of the voltage(s) in Requirement R4, Part 4.1
R5. Each Generator Owner responsible for DDR data for the electrical quantities identified in Requirement R4 shall have DDR data that meet the following:
5.1. Input sampling rate of at least 960 samples per second
5.2. Output recording rate of electrical quantities of at least 60 times per second

## Slide 9: R4 & R5 Dynamic Disturbance Recording Data
Key Takeaways
IEEE-2800-2022: measurement location is more general, but sample rate is the same as PRC-028, future units only
NOGRR255: more specific ranges than PRC-028, output rate is lower than PRC-028
Provision Data Type | Measurement/data points (as applicable) | Recording Rate | Retention | Duration | Measurement (as applicable)
Dynamic disturbance recorder (DDR) data (COMTRADE format and tabular log file) | A DDR shall capture the specified plant-level data continuously at the point of measurement. This data can be used for multiple purposes including event analysis and disturbance-based model verification. Data points shall include: - Time stamp - Bus voltage phasor (phase quantities and positive-sequence) - Bus frequency - Current phasor (phase quantities and positive-sequence) - Calculated active and reactive power output | Input: ≥ 960 samples per second output: ≥ 60 times (records) per second, continuous149 | 1 year | NA149 | Subclause 4.4, Table 2
NOGRR255
6.1.3.1 Dynamic Disturbance Recording Equipment Requirements
6.1.3.1.1 Recording and Triggering Requirements
(1) Dynamic disturbance recording equipment shall:
(a) Have either continuous data recording or triggering for at least the following:
(i) Any phase under-voltage below 0.85 p.u. for two cycles or longer;
(ii) Phase under-voltage below 0.9 p.u. for two cycles or longer;
(ii) Phase under-voltage that would trigger Under-Voltage Load Shed (UVLS);
(iii) Any phase over-voltage greater than 1.15 p.u. for two cycles or longer;
(iv) Frequency below 59.5 Hz or above 60.5 Hz; and
(v) Frequency rate of change for low frequency of -0.08125 Hz/sec or high frequency of 0.125 Hz/sec;
(vi) ERCOT must review and approve any requested deviations from the above-referenced requirements.
(vii) Additional triggering in excess of the minimums set forth in paragraph (a) above are permitted and do not require ERCOT’s review and approval.(b) Triggered record lengths of at least three minutes;
(c) A minimum output recording rate of 30 samples per second; and
(d) A minimum input sampling rate of 960 samples per second.
IEEE-2800-2022
Table 19—Measurement data

## Slide 10: R6 Time Synchronization
R6. Each Generator Owner shall time synchronize all SER, FR, and DDR data to meet the following:
6.1. Synchronization to Coordinated Universal Time (UTC) with or without a local time offset
6.2. The IBR unit synchronized device clock accuracy within ± 100 milliseconds of UTC. For all other devices, synchronized device clock accuracy within ± 1 milliseconds of UTC
IEEE-2800-2022
11. Measurement data for performance monitoring and validation
All IBR plant–level monitoring devices (sequence of event recorder, digital fault recorder, dynamic disturbance recorder, and power quality meter) shall be synchronized to UTC with ± 1 μs time accuracy, preferably using IEEE 1588–compliant devices, that implement either the IEEE C37.238 or IEC/IEEE 61850-9-3 application profiles intended for the utility industry.
The IBR unit–level monitoring devices shall be synchronized to UTC with ± 100 μs time accuracy.
NOGRR255
6.1.4.1 Fault Recording and Sequence of Events Recording Equipment Requirements
(1) Required fault recording equipment shall be time synchronized with a Global Positioning System-based clock, or ERCOT approved alternative, with synchronized device clock accuracy and performance within +/- 100 microseconds of Coordinated Universal Time (UTC), with or without a local time offset for Central Prevailing Time (CPT).
(2) Required sequence of events recording equipment shall be time synchronized with a Global Positioning System-based clock, or ERCOT-approved alternative, with +/- 100 microseconds of Coordinated Universal Time (UTC), with or without a local time offset for Central Prevailing Time (CPT).
Key Takeaways
IEEE-2800-2022: requires higher accuracy microseconds vs milliseconds in PRC-028
NOGRR255: requires higher accuracy microseconds vs milliseconds in PRC-028

## Slide 11: R7 Requested Data
R7. Each Generator Owner shall provide all requested SER, FR, and DDR data to its Transmission Planner, Planning Coordinator, Transmission Operator, Balancing Authority, Reliability Coordinator, Regional Entity, or NERC in accordance with the following:
7.1. Data shall be retrievable for the period of 20 calendar days, inclusive of the day the data was recorded
7.2. Data subject to Part 7.1 shall be provided within 15 calendar days of a request unless an extension is granted by the requestor
7.3. SER data shall be provided in ASCII4 Comma Separated Value (CSV) format following Attachment 1
7.4. FR data shall be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later
7.5. DDR data shall be provided either in CSV format with appropriate headers or in electronic files that are formatted in conformance with C37.111, IEEE Standard Common Format for Transient Data Exchange (COMTRADE), revision C37.111-1999 or later
7.6. Data files shall be named in conformance with C37.232, IEEE Standard for Common Format for Naming Time Sequence Data Files (COMNAME), revision C37.232-2011 or later

## Slide 12: R7 Requested Data
NOGRR255
6.1.2.4 Fault Recording and Sequence of Events Recording Data Retention and Reporting Requirements
(1) Each Transmission Facility owner and Generation Resource owner shall, upon request, provide to ERCOT fault recording and sequence of events recording data for the Transmission Elements identified in these requirements as follows:
(a) Data shall be maintained and retrievable for at a minimum:
(i) Twenty calendar days, including the day the data was recorded, for fault recording and sequence of events recording equipment installed on or replaced after June 1, 2024;
(ii) Ten calendar days, including the day the data was recorded, for fault recording and sequence of events recording equipment installed prior to June 1, 2024;
(b) Data subject to paragraph (1)(a) above will be provided within seven calendar days of request unless the requestor grants an extension;
6.1.3.1.4 Data Retention and Data Reporting Requirements
(2) Each affected Market Participant shall provide to the requesting Entity, upon request, dynamic disturbance recording data to the requesting entity, as follows:
(a) Data must be retrievable for ten calendar days, including the day the data was recorded;
(b) Data subject to paragraph (2)(a) above within seven calendar days of a request unless the requestor grants an extension;
(c) Dynamic disturbance recording data in electronic files formatted in conformance with IEEE C37.111, revision C37.111-1999 or later;
(d) Data files named in conformance with IEEE C37.232, revision C37.232-2011 or later.
Key Takeaways
IEEE-2800-2022: data retention longer than PRC-028, no reporting deadline
NOGRR255: Future SER and FR data retention same as, reporting deadline shorter than PRC-028; Existing SER and FR, and future/existing DDR data retention and reporting deadline shorter than PRC-028
Provision data type | Retention
Sequence of events recording (SER) data (tabular log file, time tag shall have an accuracy of one millisecond or less) | 90 days
Digital fault recording (DFR) data (COMTRADE format and tabular log file) | 90 days
Dynamic disturbance recorder (DDR) data (COMTRADE format and tabular log file) | 1 year
IEEE-2800-2022
Table 19—Measurement data

## Slide 13: R8 Failure Of The Recording Capability
R8. Each Generator Owner shall, upon the discovery of a failure of the recording capability for the SER, FR, or DDR data:
• Restore the recording capability within 90 calendar days, or
• Submit a Corrective Action Plan (CAP) to the Regional Entity within 90 calendar days and then implement it according to CAP timeline.
NOGRR255
6.1.5 Maintenance and Testing Requirements
(1) Each Market Participant with dynamic disturbance recording, phasor measurement recording, fault recording, or sequence of events recording equipment identified by Section 6.1.2, Fault Recording and Sequence of Events Recording Equipment, Section 6.1.3, Dynamic Disturbance Recording Equipment Including Phasor Measurement Unit Equipment, and Section 6.1.4, Fault Recording, Sequence of Events Recording, and Phasor Measurement Unit Requirements for Inverter-Based Resources (IBRs), shall maintain and test its equipment as follows:
(a) Calibrate or configure the devices at installation and when records from the equipment indicate a calibration or configuration problem;
(b) To ensure data stored locally is available upon request by verifying data availability and quality at least once every 60 calendar days, or institute an automated notification system to detect when the equipment ceases recording required data or fails to timely refresh the data.
(2) Each Market Participant with dynamic disturbance recording equipment, phasor measurement recording, fault recording, or sequence of events recording equipment identified by Section 6.1.2, Section 6.1.3, and Section 6.1.4 shall, within 90 calendar days of discovering a failure of the required data production, either:
(a) Restore the recording capability, or
(b) Notify and submit to ERCOT a plan and timeline for restoring the equipment recording capabilities.
Key Takeaways
IEEE-2800-2022: no repair deadline
NOGRR255: continuous monitoring, and similar repair deadline to PRC-028

## Slide 14: Contact
Eric Newnam
(512) 583-4945
Eric.Newnam@texasre.org

## Slide 15
Questions?