## Slide 1
Oncor Tredway 138-kV Switch and Expanse to Tredway 138-kV 2nd Circuit Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
April 23, 2025

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Tredway 138-kV Switch and Expanse to Tredway 138-kV 2nd Circuit Project for Regional Planning Group (RPG) review in September 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $119.03 million and will not require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues in the Borden, Howard, and Martin Counties in the Far West Weather Zone

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Borden, Howard, and Martin Counties in the Far West Weather Zone
System improvement is needed to meet reliability planning criteria
Contingency Category* | Unsolved Power Flow | Voltage Violations | Thermal Overloads
P1 | None | 5 | 5
P3 (G-1+N-1)* | None | 6*** | 5***
P6.2 (X-1+N-1)** | None | 6*** | 5***
P7 | None | None | None
*G-1 Generators studied: Odessa, Permian Basin, Juno Solar S1, Long Draw Solar S2, Morgan Creek N1
**X-1 Transformers studied: Expanse X2, Long Draw X1, Morgan Creek X1, Odessa X1
***Violations seen in the basecase under P1 events were also seen under G-1 and X-1 events

## Slide 5: Comparison of Project Options
ERCOT analyzed five options and short-listed three options
Among the three short-listed options, Option 1 addresses the reliability violations, improves long-term load-serving capability without requiring a CCN and ensures ERCOT and NERC Reliability under the maintenance sensitivity.
ERCOT recommends Option 1 as the preferred option
* Cost estimates and Feasibility were provided by TSPs
 | Option 1 | Option 3 | Option 5
Addresses Project Needs | Yes | Yes | Yes
Met ERCOT and NERC Reliability Criteria | Yes | Yes | Yes
Secured Under Maintenance Sensitivity | Yes | No | No
Improves Long-Term Load-Serving Capability | Best | Yes | Yes
CCN Needed (Miles) | No | Yes (~24.4) | No
Capital Cost Estimates* (~$M) | 119.03 | 241.7 | 86.0
Feasible* | Yes | Yes | Yes

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1 to address reliability needs in Borden, Howard, and Martin Counties in the Far West Weather Zone
TSPs expect to implement the upgrades by December 2025
Estimated Capital Cost: $119.03 million

## Slide 9: ERCOT Recommendation
Establish a new Oncor Tredway 138-kV Switch, approximately 0.5 miles north of Oncor’s existing Vealmoor 345/138-kV Switch;
Construct a new Tredway to Structure 10/7 138-kV transmission line on double-circuit capable structures with one circuit in place, with normal and emergency ratings of 614 MVA or greater, approximately 0.6-mile;
  Disconnect the existing Luther to Vealmoor 138-kV transmission line at Vealmoor 138-kV Switch, and terminate into the new Oncor Tredway 138-kV Switch;
Construct a new Tredway to Vealmoor Autotransformer #1 138-kV tie line on double-circuit capable structures with one circuit in place, with normal and emergency ratings of 828 MVA or greater, approximately 0.4-mile;
Construct a new Tredway to Vealmoor Autotransformer #2 138-kV tie line on double-circuit capable structures with one circuit in place, with normal and emergency ratings of 828 MVA or greater, approximately 0.4-mile;
Construct a new Tredway to Structure 1/3 138-kV transmission line on double-circuit capable structures with both circuits in place, with normal and emergency ratings of 614 MVA or greater, approximately 0.3-mile. The existing Structure 1/3 is located on the existing Buzzard Draw to Koch Tap to Vealmoor 138-kV transmission line;
  Disconnect the existing Buzzard Draw to Koch Tap to Vealmoor transmission line at Vealmoor 138-kV Switch, and terminate into the new Oncor Tredway 138-kV Switch;

## Slide 10: ERCOT Recommendation (Continued)
Rebuild the existing Expanse to Buzzard Draw to Structure 1/3 138-kV transmission line on double-circuit capable structures with both circuits in place, with normal and emergency ratings of 614 MVA or greater, approximately 28.8-mile, creating the Expanse to Tredway North and South 138-kV transmission lines. The new north circuit flies by Buzzard Draw 138-kV Switch, establishing the new Tredway to Expanse 138-kV double-circuit transmission line;
Remove the circuit breakers at the existing Brown 138-kV Substation and connect Brown 138-kV to the north Expanse to Tredway 138-kV transmission line;
Reconnect the existing Oceanic Point of Delivery (POD) 138-kV to the new north Expanse to Tredway 138-kV transmission line;
Reconfigure the existing Flat Land 138-kV substation from a single-tap configuration to a double-tap configuration so the substation is served from both of the Expanse to Tredway 138-kV circuits;
Construct a new Expanse to Lenorah POD 138-kV transmission line on double-circuit capable structures with one circuit in place, with normal and emergency ratings of 614 MVA or greater, approximately 0.6-mile;
  Disconnect the existing Lenorah POD from the existing Expanse to Buzzard Draw 138-kV transmission line so it is served radially from Expanse Switch;

## Slide 11: ERCOT Recommendation (Continued)
Construct a new Expanse to Merrick POD 138-kV transmission line on double-circuit capable structures with one circuit in place, with normal and emergency ratings of 614 MVA or greater, approximately 1.0-mile;
  Disconnect the existing Merrick POD from the existing Expanse to Buzzard Draw 138-kV transmission line so it is served radially from Expanse Switch;
Install five 138-kV, 3200 A circuit breakers at Expanse 345/138 kV Switch; and
Install two 55.2 MVAr capacitor banks at Expanse 345/138-kV Switch.

## Slide 12: ERCOT Recommendation